## EFV Calculator
Analysis Notes:
Type Notes Here
[5 empty] | Min.Trip SCFH | Max.Trip SCFH | Protected EQ FT
P
|  |  |  | 5 | 424.1856 | 636.2784 | 3819.1428
[5 empty] | 366.3903 | 549.5854 | 0
Minimum EFV Inlet Pressure (psig): |  |  | 10 | 10 | 475 | 712.5 | 7878.2832
[5 empty] | 366.3903 | 549.5854 | 0
Gas Specific Gravity: |  |  | 0.6 | 15 | 520.8806 | 781.3209 | 11652.6148
[5 empty] | 366.3903 | 549.5854 | 0
Gas Temperature (°F): |  |  | 60 | 20 | 563.0348 | 844.5522 | 15279.0455
[5 empty] | 366.3903 | 549.5854 | 0
Min Trip Flow (SCFH): |  |  | 475 | 30 | 639.055 | 958.5825 | 22325.381
Max Trip Flow (SCFH): |  |  | 712.5 | 40 | 706.9473 | 1060.4209 | 29268.363
Cushion between Min Trip Flow and Load: |  |  | 10% | 50 | 768.8677 | 1153.3016 | 36196.4663
Max Anticipated Load (SCFH): |  |  | 431.8182 | 60 | 826.1603 | 1239.2404 | 43145.956
Max. Equiv. Service Line Protected (FT): |  |  | 7878.2832 | 70 | 879.7295 | 1319.5942 | 50132.7153
|  |  |  | 80 | 930.2188 | 1395.3282 | 57163.6414
Desired Load: |  |  | 390 | 90 | 978.1054 | 1467.1581 | 64241.3461
Cushion between Min Trip Flow and DesiredLoad: |  |  | 21.79% | 100 | 1023.7545 | 1535.6318 | 71366.2986
Desired Min Pressure at Regulator (psig): |  |  | 2.5 | 125 | 1129.8368 | 1694.7552 | 89379.9984
Estimated Max Equiv. Service Line Length (FT): |  |  | 18319.5616
| System Pressure (psig): |  | 10
| Service Line Length (FT): |  | 100
Reset Time at 45% Max Allowed Bypass: |  |  | 0:05
Reset Time at | 20% | Max Allowed Bypass: | 0:11
Service Pipe Size
EFV Series
Warning - The calculations in this program are, to the best of our knowledge, correct and represent various calculations as determined by R. W. Lyall & Company Inc. R. W. Lyall accepts no responsibility for the use and/or application of this program. Each project has its own set of variables and conditions. Interpretation of these variables is important. The user operator must apply proper engineering when selecting excess flow valves for use in their system.
Greg Goble
Version 8a

## Pressure Drop
EFV Series:
Analysis Notes:
Type Analysis Notes Here
Desired Flow Rate (SCFH): |  | 400
EFV Min Trip Flow Rate (SCFH): |  | 474.8076
| Inlet Pressure (psig): | 10
Gas Specific Gravity: |  | 0.6
Gas Temperature (°F): |  | 60
EFV Pressure Drop
| at Desired Flow Rate (IWC): | 7.2937
| at Desired Flow Rate (psi): | 0.2635
| at EFV Min Trip Flow Rate (IWC): | 10.277
| at EFV Min Trip Flow Rate (psi): | 0.37128
Warning - The calculations in this program are, to the best of our knowledge, correct and represent various calculations as determined by R. W. Lyall & Company Inc. R. W. Lyall accepts no responsibility for the use and/or application of this program. Each project has its own set of variables and conditions. Interpretation of these variables is important. The user operator must apply proper engineering when selecting excess flow valves for use in their system.

## What's New
Version 8a
Gasbreaker Umac EFV models were added to the calculator based on 2018 Flow Test Data.
Calculations for Equivalent Protected Length were standardized using the Nominal Wall Thickness for both Plastic and Steel pipe sizes listed. Becuase of this some Protected Length calculations will be different than previous versions.

## Data and Formulas (hidden)
EFV Calculator Data |  |  |  | Calculations & Constants | [5 empty] | Lookup Values |  |  |  | Reset Curve Coeff. |  |  | Graph Labels | [6 empty] | Graph and Output Data |  |  |  |  | Pressure Drop Chart | Pressure Drop Data |  |  | Lookup Values
Selected EFV Size |  | 8 |  | N7 - Numeric Constant |  |  |  | 1360 |  | Flow Coefficient - Cv |  | 2.0359 |  | A= | -0.19 |  | Anticipated Load w/ 10% Margin | [6 empty] | Trip Curve Graph | [5 empty] | Selected EFV Size |  | 8 | Flow Coefficient - Cv | 2.0359
Selected Pipe Size |  | 7 |  | Temp °R Upstream |  |  |  | 519.67 |  | Pressure Drop - DP |  | 10.2956 |  | B= | 0.1028 | [10 empty] | P | Pt #1 | Pt #2 |  | Selected Flowrate |  | 400 | Pressure Drop - DP (IWC) | 10.2956
Adjusted Pipe Size |  | 7 | [7 empty] | Max Limit - (% of Min) |  | 50% |  | C= | -0.0059 |  | 45% Bypass Flow | [6 empty] | Min Trip Flow @ P |  | 10 | 475 |  |  | Target Pressure |  | 10
|  |  |  | Open to Atmosphere Pressure |  |  |  | 0 |  | Bypass Rate |  | 0.45 |  | D= | 0.000156 |  | 20% Bypass Flow | [6 empty] | Max Trip Flow @ P |  | 10 | 712.5 | [5 empty] | Shift Coefficient A | 0
Min System Pressure |  | 10 | [11 empty] | E= | -4e-07 | [8 empty] | Max Anticipated Load |  | 0 | 431.8182 | 390 |  | Specific Gravity |  | 0.6 | Shift Coefficient B | 0
Specific Gravity |  | 0.6 |  | Conversion ft3 to dry gal |  |  |  | 6.428 |  | Pipe Inside Diameter |  | 1.061 | [13 empty] | 125 | 431.8182 | 390 |  | Gas Temperature (°F) |  | 60 | Shift Coefficient C | 0
Gas Temperature (°F) |  | 60 |  | Volume added for the Nipple |  |  |  | 15.5 | [15 empty] | Equivalent Service Length Curve Graph
|  |  |  | Volume of Pipe (Dry Gallon) |  |  |  | 4.0047 |  | Shift Coefficient A |  | 0 | [11 empty] | Equiv. Length @ Inlet Pressure |  | 10 | 7878.2832 |  |  | Calculations
System Pressure |  | 10 | [7 empty] | Shift Coefficient B |  | 0 | [11 empty] | EFV Reset Time Chart
Service Line Length |  | 100 |  | Calculated Minimum Pressure @ max trip |  |  |  | 0.83606 |  | Shift Coefficient C |  | 0 | [11 empty] | Target Reset Point |  | 45% | 4.8512 | 0:05 |  | Min EFV Trip Flow |  | 474.8076 | DP (IWC) | 7.2937
Estimated Bypass |  | 0.2 |  | Calculated Minimum Pressure @ desired load |  |  |  | 9.7495 | [15 empty] | User Reset Point |  | 20% | 10.9153 | 0:11 |  | Flowrate Step Size |  | 3.7985 | DP (psi) | 0.2635
|  |  |  | Calc Max Pressure at Regulator @ desired load |  |  |  | 9.2495 | [24 empty] | DP (IWC) Actual | 10.277
Desired Load: |  | 390 |  | Estimated Equiv. Service Line Length (FT): |  |  |  | 18319.5616 | [24 empty] | DP (psi) Actual | 0.37128
Desired Pressure at Regulator (psig): |  | 2.5
Pressure Drop Chart
EFV Size Data Table | [8 empty] | P | Trip Flow Calculations |  |  |  | Equiv. Ft of Pipe |  | Graph Index | Reset Time Calculations | [6 empty] | Data Being Graphed | [5 empty] | Flowrate (SCFH) | DP (psi) | DP (IWC) |  | 0.83538
# | EFV Size | Cv | DP (IWC) | Max Limit % | Bypass Rate | Shift Coefficients |  |  |  | x | Shift Curve | Min Trip Flow | Max Trip Flow | P (adj for EFV DP) | Equiv. Length (ft) (IGT) |  | Intercept | Slope | Bypass CFH@10 | % Max Bypass | Bypass CFH @ P | Time to Reset | Reset (H:MM:SS) | P | Min Trip | Max Trip | Eq Ft Service
[6 empty] | a | b | c | [21 empty] | 0 | 0 | 0
1 | EFV II Series 375 | 1.6381 | 9.9123 | 46.67% | 45% |  |  |  | 0 | 0.025301 | 0 | 366.3903 | 549.5854 | 0 | 0 | 1 | 13.1 | 0.69 | 20 | 100% | 20 | 2.1831 | 0:02 | 1 | 378.6557 | 567.9836 | 162.5831 |  |  | 3.7985 | 2.3762e-05 | 0.00065773
2 | EFV II Series 400 | 1.6381 | 11.278 | 37.5% | 45% |  |  |  | 1 | 0.023688 | 0 | 378.6557 | 567.9836 | 0.16406 | 162.5831 | 2 | 12.4882 | 0.65118 | 19 | 95% | 19 | 2.298 | 0:02 | 2 | 390.5361 | 585.8042 | 1128.0963 |  |  | 7.5969 | 9.5048e-05 | 0.0026309
3 | EFV II Series 450 | 1.6381 | 14.2738 | 22.2% | 45% |  |  |  | 2 | 0.022269 | 0 | 390.5361 | 585.8042 | 1.164 | 1128.0963 | 3 | 11.834 | 0.6166 | 18 | 90% | 18 | 2.4256 | 0:02 | 3 | 402.0657 | 603.0985 | 2055.3519 |  |  | 11.3954 | 0.00021386 | 0.0059195
4 | EFV II Series 775 | 1.6381 | 42.3367 | 50% | 45% |  |  |  | 3 | 0.02101 | 0 | 402.0657 | 603.0985 | 2.164 | 2055.3519 | 4 | 11.1448 | 0.58552 | 17 | 85% | 17 | 2.5683 | 0:03 | 4 | 413.2737 | 619.9105 | 2950.682 |  |  | 15.1938 | 0.00038019 | 0.010524
5 | EFV I Series 350 | 1.5437 | 9.7225 | 50% | 45% |  |  |  | 4 | 0.019886 | 0 | 413.2737 | 619.9105 | 3.164 | 2950.682 | 5 | 10.4284 | 0.55716 | 16 | 80% | 16 | 2.7288 | 0:03 | 5 | 424.1856 | 636.2784 | 3819.1428 |  |  | 18.9923 | 0.00059405 | 0.016443
6 | EFV I Series 350 (1 IPS) | 1.5049 | 12.379 | 50% | 45% |  |  |  | 5 | 0.018876 | 0 | 424.1856 | 636.2784 | 4.164 | 3819.1428 | 6 | 9.6925 | 0.53075 | 15 | 75% | 15 | 2.9107 | 0:03 | 6 | 434.8238 | 652.2357 | 4664.8189 |  |  | 22.7908 | 0.00085543 | 0.023678
7 | EFV I Series 450 (1 IPS) | 1.9031 | 10.5751 | 25% | 45% |  |  |  | 6 | 0.017964 | 0 | 434.8238 | 652.2357 | 5.164 | 4664.8189 | 7 | 8.945 | 0.5055 | 14 | 70% | 14 | 3.1187 | 0:03 | 7 | 445.2079 | 667.8118 | 5491.0452 |  |  | 26.5892 | 0.0011643 | 0.032229
8 | EFV I Series 475 | 2.0359 | 10.2956 | 50% | 45% |  |  |  | 7 | 0.017136 | 0 | 445.2079 | 667.8118 | 6.164 | 5491.0452 | 8 | 8.1939 | 0.48061 | 13 | 65% | 13 | 3.3586 | 0:03 | 8 | 455.3552 | 683.0328 | 6300.57 |  |  | 30.3877 | 0.0015208 | 0.042095
9 | EFV I Series 475 (1 IPS) | 1.9031 | 14.3939 | 50% | 45% |  |  |  | 8 | 0.01638 | 0 | 455.3552 | 683.0328 | 7.164 | 6300.57 | 9 | 7.4473 | 0.45527 | 12 | 60% | 12 | 3.6384 | 0:04 | 9 | 465.2813 | 697.9219 | 7095.6781 |  |  | 34.1861 | 0.0019247 | 0.053276
10 | EFV I Series 775 | 2.3252 | 21.011 | 50% | 45% |  |  |  | 9 | 0.015689 | 0 | 465.2813 | 697.9219 | 8.164 | 7095.6781 | 10 | 6.7132 | 0.42868 | 11 | 55% | 11 | 3.9692 | 0:04 | 10 | 475 | 712.5 | 7878.2832 |  |  | 37.9846 | 0.0023762 | 0.065773
11 | EFV I Series 775 (1 IPS) | 2.4133 | 23.7398 | 50% | 45% |  |  |  | 10 | 0.015053 | 0 | 475 | 712.5 | 9.1639 | 7878.2832 | 11 | 6 | 0.4 | 10 | 50% | 10 | 4.3661 | 0:04 | 11 | 484.5238 | 726.7857 | 8650.0002 |  |  | 41.7831 | 0.0028752 | 0.079585
12 | EFV I Series 1100 | 2.6967 | 31.4703 | 32% | 45% |  |  |  | 11 | 0.014468 | 0 | 484.5238 | 726.7857 | 10.1639 | 8650.0002 | 12 | 5.316 | 0.3684 | 9 | 45% | 9 | 4.8512 | 0:05 | 12 | 493.864 | 740.796 | 9412.2004 |  |  | 45.5815 | 0.0034217 | 0.094713
13 | EFV I Series 1200 | 2.6967 | 37.4522 | 50% | 45% |  |  |  | 12 | 0.013925 | 0 | 493.864 | 740.796 | 11.1639 | 9412.2004 | 13 | 4.6697 | 0.33303 | 8 | 40% | 8 | 5.4577 | 0:05 | 13 | 503.0308 | 754.5461 | 10166.055 |  |  | 49.38 | 0.0040158 | 0.11116
14 | EFV I Series 1200 (1 IPS) | 2.7208 | 44.5161 | 50% | 45% |  |  |  | 13 | 0.013423 | 0 | 503.0308 | 754.5461 | 12.1639 | 10166.055 | 14 | 4.0695 | 0.29305 | 7 | 35% | 7 | 6.2373 | 0:06 | 14 | 512.0335 | 768.0502 | 10912.5702 |  |  | 53.1784 | 0.0046573 | 0.12891
15 | EFV I Series 1800 | 2.7088 | 83.0852 | 50% | 45% |  | 4.877 | -44.103 | 14 | 0.012955 | 0 | 512.0335 | 768.0502 | 13.1639 | 10912.5702 | 15 | 3.5242 | 0.24758 | 6 | 30% | 6 | 7.2769 | 0:07 | 15 | 520.8806 | 781.3209 | 11652.6148 |  |  | 56.9769 | 0.0053464 | 0.14799
16 | EFV I Series 2600 | 3.49 | 104.9708 | 25% | 45% |  |  |  | 15 | 0.012518 | 0 | 520.8806 | 781.3209 | 14.1639 | 11652.6148 | 16 | 3.0425 | 0.19575 | 5 | 25% | 5 | 8.7322 | 0:09 | 16 | 529.5799 | 794.3699 | 12386.9421 |  |  | 60.7754 | 0.006083 | 0.16838
17 | UMAC Series 300 | 1.673 | 13.6838 | 35% | 45% |  |  |  | 16 | 0.01211 | 0 | 529.5799 | 794.3699 | 15.1639 | 12386.9421 | 17 | 2.6332 | 0.13668 | 4 | 20% | 4 | 10.9153 | 0:11 | 17 | 538.1387 | 807.208 | 13116.2087 |  |  | 64.5738 | 0.0068672 | 0.19008
18 | UMAC Series 350 | 1.048 | 27.5531 | 40% | 45% |  |  |  | 17 | 0.011728 | 0 | 538.1387 | 807.208 | 16.1639 | 13116.2087 | 18 | 2.3052 | 0.06948 | 3 | 15% | 3 | 14.5537 | 0:15 | 18 | 546.5634 | 819.8451 | 13840.9887 |  |  | 68.3723 | 0.0076989 | 0.2131
19 | UMAC Series 400 | 0.657 | 70.1071 | 40% | 45% |  |  |  | 18 | 0.01137 | 0 | 546.5634 | 819.8451 | 17.1639 | 13840.9887 | 19 | 1.7 | 0.03 | 2 | 10% | 2 | 21.8306 | 0:22 | 19 | 554.8602 | 832.2903 | 14561.7862 |  |  | 72.1708 | 0.008578 | 0.23744
20 | UMAC Series 550 | 1.075 | 49.5087 | 40% | 45% |  |  |  | 19 | 0.011032 | 0 | 554.8602 | 832.2903 | 18.1639 | 14561.7862 | 20 | 0.85 | 0.015 | 1 | 5% | 1 | 43.6612 | 0:44 | 20 | 563.0348 | 844.5522 | 15279.0455 |  |  | 75.9692 | 0.0095048 | 0.26309
21 | UMAC Series 700 | 2.835 | 11.5309 | 40% | 45% |  |  |  | 20 | 0.010714 | 0 | 563.0348 | 844.5522 | 19.1639 | 15279.0455 | 21 | [7 empty] | 21 | 571.0923 | 856.6385 | 15993.1593 |  |  | 79.7677 | 0.010479 | 0.29006
22 | UMAC Series 800 | 1.007 | 119.3696 | 40% | 45% |  |  |  | 21 | 0.010414 | 0 | 571.0923 | 856.6385 | 20.1639 | 15993.1593 | 22 | [7 empty] | 22 | 579.0378 | 868.5567 | 16704.4757 |  |  | 83.5661 | 0.011501 | 0.31834
23 | UMAC Series 1100 | 4.405 | 11.7941 | 40% | 45% |  |  |  | 22 | 0.01013 | 0 | 579.0378 | 868.5567 | 21.1639 | 16704.4757 | 23 | [7 empty] | 23 | 586.8757 | 880.3136 | 17413.3046 |  |  | 87.3646 | 0.01257 | 0.34794
24 | UMAC Series 1800 | 4.133 | 44.2896 | 40% | 45% |  |  |  | 23 | 0.0098613 | 0 | 586.8757 | 880.3136 | 22.1639 | 17413.3046 | 24 | [7 empty] | 24 | 594.6103 | 891.9155 | 18119.9221 |  |  | 91.1631 | 0.013687 | 0.37885
25 | UMAC Series 2600 | 3.853 | 86.1235 | 32% | 45% |  |  |  | 24 | 0.0096064 | 0 | 594.6103 | 891.9155 | 23.1639 | 18119.9221 | 25 | [7 empty] | 25 | 602.2456 | 903.3684 | 18824.575 |  |  | 94.9615 | 0.014851 | 0.41108
26 | UMAC Series 5500(1.25IP) | 8.512 | 78.9651 | 40% | 45% |  |  |  | 25 | 0.0093643 | 0 | 602.2456 | 903.3684 | 24.1639 | 18824.575 | 26 | [7 empty] | 26 | 609.7852 | 914.6779 | 19527.4847 |  |  | 98.76 | 0.016063 | 0.44462
27 | UMAC Series 5500(2IP) | 24.594 | 9.4589 | 40% | 45% |  |  |  | 26 | 0.0091342 | 0 | 609.7852 | 914.6779 | 25.1639 | 19527.4847 | 27 | [7 empty] | 27 | 617.2328 | 925.8492 | 20228.8499 |  |  | 102.5584 | 0.017322 | 0.47948
28 | UMAC Series 10000 | 25.86 | 28.2824 | 40% | 45% |  |  |  | 27 | 0.0089151 | 0 | 617.2328 | 925.8492 | 26.1639 | 20228.8499 | 28 | [7 empty] | 28 | 624.5916 | 936.8874 | 20928.8493 |  |  | 106.3569 | 0.018629 | 0.51566
29 | CEFV Series 1800 | 9.0994 | 7.4011 | 50% | 65% |  |  |  | 28 | 0.0087063 | 0 | 624.5916 | 936.8874 | 27.1639 | 20928.8493 | 29 | [7 empty] | 29 | 631.8647 | 947.797 | 21627.6445 |  |  | 110.1554 | 0.019984 | 0.55315
30 | CEFV Series 2600 | 9.0994 | 15.4417 | 50% | 65% |  |  |  | 29 | 0.008507 | 0 | 631.8647 | 947.797 | 28.1639 | 21627.6445 | 30 | [7 empty] | 30 | 639.055 | 958.5825 | 22325.381 |  |  | 113.9538 | 0.021386 | 0.59195
31 | CEFV Series 3900 | 17.5739 | 9.3146 | 50% | 65% | 0.0283 | 18.369 | -186.52 | 30 | 0.0083166 | 0 | 639.055 | 958.5825 | 29.1639 | 22325.381 | 31 | [7 empty] | 31 | 646.1653 | 969.248 | 23022.1909 |  |  | 117.7523 | 0.022835 | 0.63208
32 | CEFV Series 5500 | 17.5739 | 18.5252 | 50% | 65% | 0.0283 | 18.369 | -186.52 | 31 | 0.0081346 | 0 | 646.1653 | 969.248 | 30.1639 | 23022.1909 | 32 | [7 empty] | 32 | 653.1982 | 979.7974 | 23718.1937 |  |  | 121.5507 | 0.024332 | 0.67351
[9 empty] | 32 | 0.0079604 | 0 | 653.1982 | 979.7974 | 31.1638 | 23718.1937 | 33 | [7 empty] | 33 | 660.1562 | 990.2343 | 24413.4981 |  |  | 125.3492 | 0.025877 | 0.71626
Pipe Size Data Table | [8 empty] | 33 | 0.0077935 | 0 | 660.1562 | 990.2343 | 32.1638 | 24413.4981 | 34 | [7 empty] | 34 | 667.0417 | 1000.5625 | 25108.2028 |  |  | 129.1477 | 0.027469 | 0.76033
[9 empty] | 34 | 0.0076334 | 0 | 667.0417 | 1000.5625 | 33.1638 | 25108.2028 | 35 | [7 empty] | 35 | 673.8567 | 1010.7851 | 25802.3979 |  |  | 132.9461 | 0.029108 | 0.80572
# | Pipe Size | OD | Nom. Wall | ID | Display List |  |  |  | 35 | 0.0074798 | 0 | 673.8567 | 1010.7851 | 34.1638 | 25802.3979 | 36 | [7 empty] | 36 | 680.6036 | 1020.9053 | 26496.1652 |  |  | 136.7446 | 0.030795 | 0.85241
[9 empty] | 36 | 0.0073322 | 0 | 680.6036 | 1020.9053 | 35.1638 | 26496.1652 | 37 | [7 empty] | 37 | 687.2842 | 1030.9262 | 27189.5799 |  |  | 140.543 | 0.03253 | 0.90043
1 | ½ CTS .090 | 0.625 | 0.0945 | 0.436 | ½ CTS .090 |  |  |  | 37 | 0.0071904 | 0 | 687.2842 | 1030.9262 | 36.1638 | 27189.5799 | 38 | [7 empty] | 38 | 693.9004 | 1040.8507 | 27882.7101 |  |  | 144.3415 | 0.034312 | 0.94976
2 | ½ IPS DR 9.3 | 0.84 | 0.0955 | 0.649 | ½ IPS DR 9.3 |  |  |  | 38 | 0.0070539 | 0 | 693.9004 | 1040.8507 | 37.1638 | 27882.7101 | 39 | [7 empty] | 39 | 700.4542 | 1050.6814 | 28575.6187 |  |  | 148.14 | 0.036142 | 1.0004
3 | ¾ CTS .090 | 0.875 | 0.0945 | 0.686 | ¾ CTS .090 |  |  |  | 39 | 0.0069225 | 0 | 700.4542 | 1050.6814 | 38.1638 | 28575.6187 | 40 | [7 empty] | 40 | 706.9473 | 1060.4209 | 29268.363 |  |  | 151.9384 | 0.038019 | 1.0524
4 | ¾ IPS DR 11 | 1.05 | 0.1005 | 0.849 | ¾ IPS DR 11 |  |  |  | 40 | 0.006796 | 0 | 706.9473 | 1060.4209 | 39.1638 | 29268.363 | 41 | [7 empty] | 41 | 713.3812 | 1070.0718 | 29960.9955 |  |  | 155.7369 | 0.039944 | 1.1056
5 | 1 CTS .090 | 1.125 | 0.0955 | 0.934 | 1 CTS .090 |  |  |  | 41 | 0.0066739 | 0 | 713.3812 | 1070.0718 | 40.1638 | 29960.9955 | 42 | [7 empty] | 42 | 719.7577 | 1079.6365 | 30653.5645 |  |  | 159.5353 | 0.041916 | 1.1602
6 | 1 CTS .099 | 1.125 | 0.105 | 0.915 | 1 CTS .099 |  |  |  | 42 | 0.0065562 | 0 | 719.7577 | 1079.6365 | 41.1638 | 30653.5645 | 43 | [7 empty] | 43 | 726.0781 | 1089.1171 | 31346.1143 |  |  | 163.3338 | 0.043936 | 1.2161
7 | 1 IPS DR 11 | 1.315 | 0.127 | 1.061 | 1 IPS DR 11 |  |  |  | 43 | 0.0064426 | 0 | 726.0781 | 1089.1171 | 42.1638 | 31346.1143 | 44 | [7 empty] | 44 | 732.344 | 1098.516 | 32038.6856 |  |  | 167.1323 | 0.046003 | 1.2734
8 | 1¼ IPS DR 10 | 1.66 | 0.176 | 1.308 | 1¼ IPS DR 10 |  |  |  | 44 | 0.0063328 | 0 | 732.344 | 1098.516 | 43.1638 | 32038.6856 | 45 | [7 empty] | 45 | 738.5567 | 1107.8351 | 32731.3159 |  |  | 170.9307 | 0.048118 | 1.3319
9 | 1¼ IPS DR 11 | 1.66 | 0.16 | 1.34 | 1¼ IPS DR 11 |  |  |  | 45 | 0.0062267 | 0 | 738.5567 | 1107.8351 | 44.1638 | 32731.3159 | 46 | [7 empty] | 46 | 744.7176 | 1117.0764 | 33424.0396 |  |  | 174.7292 | 0.05028 | 1.3917
10 | 2 IPS DR 11 | 2.375 | 0.229 | 1.917 | 2 IPS DR 11 |  |  |  | 46 | 0.0061241 | 0 | 744.7176 | 1117.0764 | 45.1638 | 33424.0396 | 47 | [7 empty] | 47 | 750.828 | 1126.242 | 34116.8884 |  |  | 178.5276 | 0.05249 | 1.4529
11 | NPS ¾ Sch 40 | 1.05 | 0.10594 | 0.83813 | NPS ¾ Sch 40 |  |  |  | 47 | 0.0060248 | 0 | 750.828 | 1126.242 | 46.1638 | 34116.8884 | 48 | [7 empty] | 48 | 756.889 | 1135.3335 | 34809.8915 |  |  | 182.3261 | 0.054747 | 1.5154
12 | NPS 1 Sch 40 | 1.315 | 0.12469 | 1.0656 | NPS 1 Sch 40 |  |  |  | 48 | 0.0059287 | 0 | 756.889 | 1135.3335 | 47.1638 | 34809.8915 | 49 | [7 empty] | 49 | 762.9019 | 1144.3528 | 35503.0759 |  |  | 186.1246 | 0.057052 | 1.5792
[9 empty] | 49 | 0.0058356 | 0 | 762.9019 | 1144.3528 | 48.1638 | 35503.0759 | 50 | [7 empty] | 50 | 768.8677 | 1153.3016 | 36196.4663 |  |  | 189.923 | 0.059405 | 1.6443
| Change Pipe Size Order???? | [7 empty] | 50 | 0.0057454 | 0 | 768.8677 | 1153.3016 | 49.1638 | 36196.4663 | 51 | [7 empty] | 51 | 774.7877 | 1162.1815 | 36890.0857 |  |  | 193.7215 | 0.061805 | 1.7107
[9 empty] | 51 | 0.005658 | 0 | 774.7877 | 1162.1815 | 50.1638 | 36890.0857 | 52 | [7 empty] | 52 | 780.6627 | 1170.994 | 37583.955 |  |  | 197.52 | 0.064252 | 1.7785
[9 empty] | 52 | 0.0055731 | 0 | 780.6627 | 1170.994 | 51.1638 | 37583.955 | 53 | [7 empty] | 53 | 786.4938 | 1179.7408 | 38278.0939 |  |  | 201.3184 | 0.066747 | 1.8476
[9 empty] | 53 | 0.0054908 | 0 | 786.4938 | 1179.7408 | 52.1638 | 38278.0939 | 54 | [7 empty] | 54 | 792.2821 | 1188.4231 | 38972.5201 |  |  | 205.1169 | 0.06929 | 1.9179
[9 empty] | 54 | 0.0054108 | 0 | 792.2821 | 1188.4231 | 53.1638 | 38972.5201 | 55 | [7 empty] | 55 | 798.0283 | 1197.0425 | 39667.2503 |  |  | 208.9153 | 0.07188 | 1.9896
[9 empty] | 55 | 0.0053332 | 0 | 798.0283 | 1197.0425 | 54.1638 | 39667.2503 | 56 | [7 empty] | 56 | 803.7335 | 1205.6002 | 40362.2998 |  |  | 212.7138 | 0.074517 | 2.0626
[9 empty] | 56 | 0.0052578 | 0 | 803.7335 | 1205.6002 | 55.1638 | 40362.2998 | 57 | [7 empty] | 57 | 809.3984 | 1214.0976 | 41057.6826 |  |  | 216.5123 | 0.077202 | 2.137
[9 empty] | 57 | 0.0051844 | 0 | 809.3984 | 1214.0976 | 56.1638 | 41057.6826 | 58 | [7 empty] | 58 | 815.024 | 1222.536 | 41753.4118 |  |  | 220.3107 | 0.079935 | 2.2126
[9 empty] | 58 | 0.0051131 | 0 | 815.024 | 1222.536 | 57.1638 | 41753.4118 | 59 | [7 empty] | 59 | 820.611 | 1230.9165 | 42449.4992 |  |  | 224.1092 | 0.082715 | 2.2895
[9 empty] | 59 | 0.0050437 | 0 | 820.611 | 1230.9165 | 58.1638 | 42449.4992 | 60 | [7 empty] | 60 | 826.1603 | 1239.2404 | 43145.956 |  |  | 227.9076 | 0.085543 | 2.3678
[9 empty] | 60 | 0.0049762 | 0 | 826.1603 | 1239.2404 | 59.1638 | 43145.956 | 61 | [7 empty] | 61 | 831.6725 | 1247.5087 | 43842.7922 |  |  | 231.7061 | 0.088418 | 2.4474
[9 empty] | 61 | 0.0049104 | 0 | 831.6725 | 1247.5087 | 60.1638 | 43842.7922 | 62 | [7 empty] | 62 | 837.1484 | 1255.7226 | 44540.0173 |  |  | 235.5046 | 0.091341 | 2.5283
[9 empty] | 62 | 0.0048464 | 0 | 837.1484 | 1255.7226 | 61.1638 | 44540.0173 | 63 | [7 empty] | 63 | 842.5887 | 1263.883 | 45237.6399 |  |  | 239.303 | 0.094311 | 2.6105
[9 empty] | 63 | 0.004784 | 0 | 842.5887 | 1263.883 | 62.1638 | 45237.6399 | 64 | [7 empty] | 64 | 847.9941 | 1271.9912 | 45935.6679 |  |  | 243.1015 | 0.097329 | 2.694
[9 empty] | 64 | 0.0047232 | 0 | 847.9941 | 1271.9912 | 63.1638 | 45935.6679 | 65 | [7 empty] | 65 | 853.3653 | 1280.048 | 46634.1084 |  |  | 246.8999 | 0.10039 | 2.7789
[9 empty] | 65 | 0.004664 | 0 | 853.3653 | 1280.048 | 64.1638 | 46634.1084 | 66 | [7 empty] | 66 | 858.7029 | 1288.0543 | 47332.9683 |  |  | 250.6984 | 0.10351 | 2.8651
[9 empty] | 66 | 0.0046062 | 0 | 858.7029 | 1288.0543 | 65.1638 | 47332.9683 | 67 | [7 empty] | 67 | 864.0075 | 1296.0113 | 48032.2536 |  |  | 254.4969 | 0.10667 | 2.9525
[9 empty] | 67 | 0.0045498 | 0 | 864.0075 | 1296.0113 | 66.1638 | 48032.2536 | 68 | [7 empty] | 68 | 869.2797 | 1303.9196 | 48731.9699 |  |  | 258.2953 | 0.10987 | 3.0413
[9 empty] | 68 | 0.0044947 | 0 | 869.2797 | 1303.9196 | 67.1638 | 48731.9699 | 69 | [7 empty] | 69 | 874.5202 | 1311.7803 | 49432.1222 |  |  | 262.0938 | 0.11313 | 3.1314
[9 empty] | 69 | 0.004441 | 0 | 874.5202 | 1311.7803 | 68.1638 | 49432.1222 | 70 | [7 empty] | 70 | 879.7295 | 1319.5942 | 50132.7153 |  |  | 265.8922 | 0.11643 | 3.2229
[9 empty] | 70 | 0.0043886 | 0 | 879.7295 | 1319.5942 | 69.1638 | 50132.7153 | 71 | [7 empty] | 71 | 884.908 | 1327.3621 | 50833.7533 |  |  | 269.6907 | 0.11978 | 3.3156
[9 empty] | 71 | 0.0043374 | 0 | 884.908 | 1327.3621 | 70.1638 | 50833.7533 | 72 | [7 empty] | 72 | 890.0565 | 1335.0847 | 51535.2401 |  |  | 273.4892 | 0.12318 | 3.4097
[9 empty] | 72 | 0.0042874 | 0 | 890.0565 | 1335.0847 | 71.1638 | 51535.2401 | 73 | [7 empty] | 73 | 895.1753 | 1342.763 | 52237.1792 |  |  | 277.2876 | 0.12663 | 3.505
[9 empty] | 73 | 0.0042385 | 0 | 895.1753 | 1342.763 | 72.1638 | 52237.1792 | 74 | [7 empty] | 74 | 900.2651 | 1350.3976 | 52939.5737 |  |  | 281.0861 | 0.13012 | 3.6017
[9 empty] | 74 | 0.0041907 | 0 | 900.2651 | 1350.3976 | 73.1638 | 52939.5737 | 75 | [7 empty] | 75 | 905.3262 | 1357.9893 | 53642.4264 |  |  | 284.8845 | 0.13366 | 3.6997
[9 empty] | 75 | 0.0041439 | 0 | 905.3262 | 1357.9893 | 74.1638 | 53642.4264 | 76 | [7 empty] | 76 | 910.3592 | 1365.5387 | 54345.7398 |  |  | 288.683 | 0.13725 | 3.799
[9 empty] | 76 | 0.0040983 | 0 | 910.3592 | 1365.5387 | 75.1638 | 54345.7398 | 77 | [7 empty] | 77 | 915.3645 | 1373.0467 | 55049.5161 |  |  | 292.4815 | 0.14088 | 3.8997
[9 empty] | 77 | 0.0040536 | 0 | 915.3645 | 1373.0467 | 76.1638 | 55049.5161 | 78 | [7 empty] | 78 | 920.3426 | 1380.5138 | 55753.7574 |  |  | 296.2799 | 0.14457 | 4.0016
[9 empty] | 78 | 0.0040098 | 0 | 920.3426 | 1380.5138 | 77.1638 | 55753.7574 | 79 | [7 empty] | 79 | 925.2939 | 1387.9408 | 56458.4653 |  |  | 300.0784 | 0.1483 | 4.1049
[9 empty] | 79 | 0.003967 | 0 | 925.2939 | 1387.9408 | 78.1638 | 56458.4653 | 80 | [7 empty] | 80 | 930.2188 | 1395.3282 | 57163.6414 |  |  | 303.8768 | 0.15208 | 4.2095
[9 empty] | 80 | 0.0039251 | 0 | 930.2188 | 1395.3282 | 79.1638 | 57163.6414 | 81 | [7 empty] | 81 | 935.1178 | 1402.6768 | 57869.2869 |  |  | 307.6753 | 0.1559 | 4.3153
[9 empty] | 81 | 0.0038841 | 0 | 935.1178 | 1402.6768 | 80.1638 | 57869.2869 | 82 | [7 empty] | 82 | 939.9913 | 1409.987 | 58575.4029 |  |  | 311.4738 | 0.15977 | 4.4226
[9 empty] | 82 | 0.0038439 | 0 | 939.9913 | 1409.987 | 81.1638 | 58575.4029 | 83 | [7 empty] | 83 | 944.8397 | 1417.2595 | 59281.9904 |  |  | 315.2722 | 0.1637 | 4.5311
[9 empty] | 83 | 0.0038046 | 0 | 944.8397 | 1417.2595 | 82.1638 | 59281.9904 | 84 | [7 empty] | 84 | 949.6633 | 1424.4949 | 59989.0501 |  |  | 319.0707 | 0.16766 | 4.6409
[9 empty] | 84 | 0.003766 | 0 | 949.6633 | 1424.4949 | 83.1638 | 59989.0501 | 85 | [7 empty] | 85 | 954.4625 | 1431.6937 | 60696.5826 |  |  | 322.8692 | 0.17168 | 4.7521
[9 empty] | 85 | 0.0037283 | 0 | 954.4625 | 1431.6937 | 84.1638 | 60696.5826 | 86 | [7 empty] | 86 | 959.2377 | 1438.8565 | 61404.5882 |  |  | 326.6676 | 0.17574 | 4.8645
[9 empty] | 86 | 0.0036912 | 0 | 959.2377 | 1438.8565 | 85.1638 | 61404.5882 | 87 | [7 empty] | 87 | 963.9892 | 1445.9839 | 62113.0673 |  |  | 330.4661 | 0.17985 | 4.9783
[9 empty] | 87 | 0.0036549 | 0 | 963.9892 | 1445.9839 | 86.1638 | 62113.0673 | 88 | [7 empty] | 88 | 968.7175 | 1453.0762 | 62822.02 |  |  | 334.2645 | 0.18401 | 5.0934
[9 empty] | 88 | 0.0036193 | 0 | 968.7175 | 1453.0762 | 87.1638 | 62822.02 | 89 | [7 empty] | 89 | 973.4228 | 1460.1342 | 63531.4463 |  |  | 338.063 | 0.18822 | 5.2099
[9 empty] | 89 | 0.0035844 | 0 | 973.4228 | 1460.1342 | 88.1638 | 63531.4463 | 90 | [7 empty] | 90 | 978.1054 | 1467.1581 | 64241.3461 |  |  | 341.8615 | 0.19247 | 5.3276
[9 empty] | 90 | 0.0035502 | 0 | 978.1054 | 1467.1581 | 89.1638 | 64241.3461 | 91 | [7 empty] | 91 | 982.7658 | 1474.1486 | 64951.7193 |  |  | 345.6599 | 0.19677 | 5.4466
[9 empty] | 91 | 0.0035166 | 0 | 982.7658 | 1474.1486 | 90.1638 | 64951.7193 | 92 | [7 empty] | 92 | 987.4041 | 1481.1061 | 65662.5655 |  |  | 349.4584 | 0.20112 | 5.567
[9 empty] | 92 | 0.0034837 | 0 | 987.4041 | 1481.1061 | 91.1638 | 65662.5655 | 93 | [7 empty] | 93 | 992.0207 | 1488.0311 | 66373.8844 |  |  | 353.2568 | 0.20552 | 5.6887
[9 empty] | 93 | 0.0034513 | 0 | 992.0207 | 1488.0311 | 92.1638 | 66373.8844 | 94 | [7 empty] | 94 | 996.616 | 1494.924 | 67085.6753 |  |  | 357.0553 | 0.20996 | 5.8117
[9 empty] | 94 | 0.0034195 | 0 | 996.616 | 1494.924 | 93.1638 | 67085.6753 | 95 | [7 empty] | 95 | 1001.1902 | 1501.7853 | 67797.9378 |  |  | 360.8538 | 0.21445 | 5.936
[9 empty] | 95 | 0.0033884 | 0 | 1001.1902 | 1501.7853 | 94.1638 | 67797.9378 | 96 | [7 empty] | 96 | 1005.7436 | 1508.6153 | 68510.6713 |  |  | 364.6522 | 0.21899 | 6.0616
[9 empty] | 96 | 0.0033578 | 0 | 1005.7436 | 1508.6153 | 95.1638 | 68510.6713 | 97 | [7 empty] | 97 | 1010.2764 | 1515.4146 | 69223.8749 |  |  | 368.4507 | 0.22358 | 6.1886
[9 empty] | 97 | 0.0033277 | 0 | 1010.2764 | 1515.4146 | 96.1638 | 69223.8749 | 98 | [7 empty] | 98 | 1014.789 | 1522.1835 | 69937.5479 |  |  | 372.2491 | 0.22821 | 6.3168
[9 empty] | 98 | 0.0032982 | 0 | 1014.789 | 1522.1835 | 97.1638 | 69937.5479 | 99 | [7 empty] | 99 | 1019.2816 | 1528.9225 | 70651.6894 |  |  | 376.0476 | 0.23289 | 6.4464
[9 empty] | 99 | 0.0032692 | 0 | 1019.2816 | 1528.9225 | 98.1638 | 70651.6894 | 100 | [7 empty] | 100 | 1023.7545 | 1535.6318 | 71366.2986 |  |  | 379.8461 | 0.23762 | 6.5773
[9 empty] | 100 | 0.0032407 | 0 | 1023.7545 | 1535.6318 | 99.1638 | 71366.2986 | 101 | [7 empty] | 101 | 1028.208 | 1542.312 | 72081.3744 |  |  | 383.6445 | 0.2424 | 6.7095
[9 empty] | 101 | 0.0032126 | 0 | 1028.208 | 1542.312 | 100.1638 | 72081.3744 | 102 | [7 empty] | 102 | 1032.6422 | 1548.9634 | 72796.9159 |  |  | 387.443 | 0.24722 | 6.843
[9 empty] | 102 | 0.0031851 | 0 | 1032.6422 | 1548.9634 | 101.1638 | 72796.9159 | 103 | [7 empty] | 103 | 1037.0575 | 1555.5863 | 73512.9219 |  |  | 391.2414 | 0.25209 | 6.9778
[9 empty] | 103 | 0.003158 | 0 | 1037.0575 | 1555.5863 | 102.1638 | 73512.9219 | 104 | [7 empty] | 104 | 1041.4541 | 1562.1811 | 74229.3914 |  |  | 395.0399 | 0.25701 | 7.114
[9 empty] | 104 | 0.0031314 | 0 | 1041.4541 | 1562.1811 | 103.1638 | 74229.3914 | 105 | [7 empty] | 105 | 1045.8322 | 1568.7483 | 74946.3232 |  |  | 398.8384 | 0.26197 | 7.2514
[9 empty] | 105 | 0.0031053 | 0 | 1045.8322 | 1568.7483 | 104.1638 | 74946.3232 | 106 | [7 empty] | 106 | 1050.192 | 1575.288 | 75663.7161 |  |  | 402.6368 | 0.26699 | 7.3902
[9 empty] | 106 | 0.0030795 | 0 | 1050.192 | 1575.288 | 105.1638 | 75663.7161 | 107 | [7 empty] | 107 | 1054.5338 | 1581.8007 | 76381.5688 |  |  | 406.4353 | 0.27205 | 7.5303
[9 empty] | 107 | 0.0030542 | 0 | 1054.5338 | 1581.8007 | 106.1638 | 76381.5688 | 108 | [7 empty] | 108 | 1058.8578 | 1588.2867 | 77099.8802 |  |  | 410.2337 | 0.27716 | 7.6717
[9 empty] | 108 | 0.0030293 | 0 | 1058.8578 | 1588.2867 | 107.1638 | 77099.8802 | 109 | [7 empty] | 109 | 1063.1642 | 1594.7464 | 77818.6489 |  |  | 414.0322 | 0.28231 | 7.8145
[9 empty] | 109 | 0.0030049 | 0 | 1063.1642 | 1594.7464 | 108.1638 | 77818.6489 | 110 | [7 empty] | 110 | 1067.4533 | 1601.1799 | 78537.8735 |  |  | 417.8307 | 0.28752 | 7.9585
[9 empty] | 110 | 0.0029808 | 0 | 1067.4533 | 1601.1799 | 109.1638 | 78537.8735 | 111 | [7 empty] | 111 | 1071.7252 | 1607.5878 | 79257.5528 |  |  | 421.6291 | 0.29277 | 8.1039
[9 empty] | 111 | 0.002957 | 0 | 1071.7252 | 1607.5878 | 110.1638 | 79257.5528 | 112 | [7 empty] | 112 | 1075.9801 | 1613.9701 | 79977.6854 |  |  | 425.4276 | 0.29807 | 8.2505
[9 empty] | 112 | 0.0029337 | 0 | 1075.9801 | 1613.9701 | 111.1638 | 79977.6854 | 113 | [7 empty] | 113 | 1080.2182 | 1620.3274 | 80698.2699 |  |  | 429.2261 | 0.30342 | 8.3985
[9 empty] | 113 | 0.0029107 | 0 | 1080.2182 | 1620.3274 | 112.1638 | 80698.2699 | 114 | [7 empty] | 114 | 1084.4398 | 1626.6598 | 81419.3048 |  |  | 433.0245 | 0.30881 | 8.5478
[9 empty] | 114 | 0.0028881 | 0 | 1084.4398 | 1626.6598 | 113.1638 | 81419.3048 | 115 | [7 empty] | 115 | 1088.6451 | 1632.9676 | 82140.7888 |  |  | 436.823 | 0.31425 | 8.6984
[9 empty] | 115 | 0.0028658 | 0 | 1088.6451 | 1632.9676 | 114.1638 | 82140.7888 | 116 | [7 empty] | 116 | 1092.8341 | 1639.2512 | 82862.7203 |  |  | 440.6214 | 0.31974 | 8.8504
[9 empty] | 116 | 0.0028439 | 0 | 1092.8341 | 1639.2512 | 115.1638 | 82862.7203 | 117 | [7 empty] | 117 | 1097.0072 | 1645.5108 | 83585.0979 |  |  | 444.4199 | 0.32528 | 9.0036
[9 empty] | 117 | 0.0028223 | 0 | 1097.0072 | 1645.5108 | 116.1638 | 83585.0979 | 118 | [7 empty] | 118 | 1101.1644 | 1651.7466 | 84307.9202 |  |  | 448.2184 | 0.33086 | 9.1582
[9 empty] | 118 | 0.002801 | 0 | 1101.1644 | 1651.7466 | 117.1638 | 84307.9202 | 119 | [7 empty] | 119 | 1105.306 | 1657.959 | 85031.1855 |  |  | 452.0168 | 0.33649 | 9.3141
[9 empty] | 119 | 0.0027801 | 0 | 1105.306 | 1657.959 | 118.1638 | 85031.1855 | 120 | [7 empty] | 120 | 1109.4321 | 1664.1482 | 85754.8925 |  |  | 455.8153 | 0.34217 | 9.4713
[9 empty] | 120 | 0.0027595 | 0 | 1109.4321 | 1664.1482 | 119.1638 | 85754.8925 | 121 | [7 empty] | 121 | 1113.543 | 1670.3145 | 86479.0396 |  |  | 459.6137 | 0.3479 | 9.6298
[9 empty] | 121 | 0.0027391 | 0 | 1113.543 | 1670.3145 | 120.1638 | 86479.0396 | 122 | [7 empty] | 122 | 1117.6387 | 1676.4581 | 87203.6253 |  |  | 463.4122 | 0.35367 | 9.7896
[9 empty] | 122 | 0.0027191 | 0 | 1117.6387 | 1676.4581 | 121.1638 | 87203.6253 | 123 | [7 empty] | 123 | 1121.7195 | 1682.5792 | 87928.648 |  |  | 467.2107 | 0.35949 | 9.9507
[9 empty] | 123 | 0.0026993 | 0 | 1121.7195 | 1682.5792 | 122.1638 | 87928.648 | 124 | [7 empty] | 124 | 1125.7855 | 1688.6782 | 88654.1062 |  |  | 471.0091 | 0.36536 | 10.1132
[9 empty] | 124 | 0.0026799 | 0 | 1125.7855 | 1688.6782 | 123.1638 | 88654.1062 | 125 | [7 empty] | 125 | 1129.8368 | 1694.7552 | 89379.9984 |  |  | 474.8076 | 0.37128 | 10.277
[9 empty] | 125 | 0.0026607 | 0 | 1129.8368 | 1694.7552 | 124.1638 | 89379.9984 | 126 | [7 empty] | 126 | 1129.8368 | 1694.7552 | 89379.9984
Note on A1: Bill DeKeyser: This section is the data that is entered on the main page of the EFV Calculator and is linked in the appropiate formula
Note on L1: Bill DeKeyser: This table are values used in calculations to reduce the number of lookup functions used.
Note on P1: Bill DeKeyser: These are the coefficients for the reset time curve
Note on T1: Bill DeKeyser: Provides Smart Labels for the the EFV Calculator
Note on AH1: Bill DeKeyser: Everything to the Right of this column is for the Pressure Drop Chart
Note on AJ1: Bill DeKeyser: All Data in this table is entered on Pressure Drop Tab. It is not affected by EFV Calculator entries
Note on AN1: Bill DeKeyser: This table are values used in calculations to reduce the number of lookup functions used. Same as table used for EFV Calculator, but uses EFV Series selected on Pressure Drop Tab
Note on C2: Bill DeKeyser: This is the index number selected for the EFV Size from the Calculator
Note on I2: Bill DeKeyser: Constant for SCFH, psia & °R
Note on AL2: Bill DeKeyser: Index Number from Pulldown box on Pressure Drop
Note on C3: Bill DeKeyser: This is the index number selected for the Pipe Size from the Calculator
Note on C4: Bill DeKeyser: This prevents the EFV II from being used in anything other than ½ CTS Pipe
Note on AB4: Bill DeKeyser: Creates Min Trip Flow Line
Note on I5: Bill DeKeyser: This is used for the Equivalent Service Length if an atmospheric adjustment is required
Note on AB5: Bill DeKeyser: Creates Max Trip Flow Line
Note on AB6: Bill DeKeyser: Creates Line for Load Margin and Max Anticipated Load provided by Customer
Note on I7: Bill DeKeyser: The conversion factor used in the Reset Time Calculation to get to dry gal
Note on I8: Bill DeKeyser: This is a generic fudge factor that is added to account for the volume above the nipple in Reset Time Calculations
Note on I9: Bill DeKeyser: Calculated the volume of the service and converts to Dry Gallons for Reset Time
Note on AB9: Bill DeKeyser: Creates Marker for Equivalent Length of Service Chart
Note on AL11: Bill DeKeyser: Calculated Minimum Trip Point for the EFV Selected and the conditions selected. X and shift valvues are incorporated into the formula
Note on AP11: Bill DeKeyser: Pressure Drop at the selected conditions in IWC
Note on AL12: Bill DeKeyser: To make the x-y plot of the pressure drop the Min EFV Trip Flow is divided by 125 (# points on chart) to create a step for plotting the curve.
Note on AP12: Bill DeKeyser: Pressure Drop for the selected conditions in psi
Note on AP13: Bill DeKeyser: Pressure Drop at the selected conditions in IWC
Note on T17: Bill DeKeyser: Uses Reset Curve Coefficients to plot curve. Plots against Bypass at 10 psi
Note on AB17: Bill DeKeyser: This Table removes any point where the EFV will not close due to service line pressure not being greater than the pressure drop at trip. No calculations just looking up data from Trip Flow Calculations and Equivalent Feet of Pipe Calcualtions
Note on C18: Bill DeKeyser: EFV I and EFV II Cv Values were taken from Lab Project 2012 010. CEFV Cv Values were taken from Lab Project 2012 016.
Note on D18: Bill DeKeyser: Pressure drop was measured in the same project as Cv Value. However, this value was adjusted using Goal Seek to perfectly align the trip point at 10 psig. This takes out measurement error of not being exactly at the minimum trip point and pressure when recording the data.
Note on E18: Bill DeKeyser: This is the percent that the max trip point is greater than the minimum trip point.
Note on F18: Bill DeKeyser: This value is used for the reset time calulation and should be the average for specific models
Note on G18: Bill DeKeyser: These coefficients are only needed when the empirical test data does not match the flow curve generated using the Cv Value. To create these values plot the difference between actual and theoretical trip flow. See Shift Calculations Tab
Note on M18: Bill DeKeyser: This column only calculates a value for models that have shown they do not follow the flow curve shape. See Shift Calculations Tab for how this value was generated.
Note on P18: Bill DeKeyser: This is the pressure from column K adjusted for the pressure loss of the EFV
Note on U38: Bill DeKeyser: Manually Entered Value to get Curve Shape
Note on U39: Bill DeKeyser: Manually entered Value to get curve shape
Note on D55: Goble, Greg: Made change to nominal wall adding half the wall tolerance.
Note on F55: Bill DeKeyser: This is the list used in the drop box. When EFV II selected ½ CTS is the only choice.

## Shift Calculations (hidden)
EFV I Series 1800 | [14 empty] | EFV I Series 1800 | CEFV 3900 & 5500 Shift | [23 empty] | CEFV 3900 & 5500 Shift
| Data -Old EFV Calculator |  | Flow Data from CV Calculation | [8 empty] | Test Data (8-3-12) |  | The Curve Fit Data from the Old EFV Calculator was compared to the theoretical Curve generated by the Cv Value. The difference between these two values was plotted and the equation for the linear fit of these data points was used to generate a shift for the CV generated Curve. The shifted Cv Curve was then plotted vs test data to show that the shape holds up to empirical testing. The green data is an offset curve at 41% of the minimum trip flow to simulate what perfect test data should have plotted on the chart. It was very close to the actual data points. | [24 empty] | A similar approach was used to calculate the needed shift for the 3900 and 5500 CEFV. The Cv Curve did not fit match the empirical data so a shift was created by taking an average of the 3900 from 1¼ and 2 IPS sizes and the 5500 from 1¼ and 2 IPS, then taking the difference at these points from the Cv Curve. The differences for the 3900 and 5500 were then averaged and plotted with a 2nd order polynomial was used to fit the difference data. This polynomial was used to create the shift coefficients that are listed in the boxes. They are a little low for the 5500 and a little high for the 3900 but over estimate the two models very well. The new shifted max and min trip are plotted on the chart along with data points so the shift can be seen. The shift moves the shifted test curve to follow the data fairly close.
| Curve Fit Coefficients |  | Values Used for Calculation |  |  |  | Shift Values |  |  |  |  | Pressure | Flowrate |  |  |  | Values Used for Calculation |  |  |  | Values Used for Calculation | [7 empty] | Shift Values |  |  |  |  | Shift Values
| a = | 1610 | Numeric Constant |  | 1360 |  | Shift Coefficient A |  | 4.877 |  |  | 9.94 | 2539.708 |  |  |  | Numeric Constant |  | 1360 |  | Numeric Constant |  | 1360 | [5 empty] | Shift Coefficient A |  | 0.0283 |  |  | Shift Coefficient A |  | 0.0283
| b = | 58.4392 | Temp °R Upstream |  | 519.67 |  | Shift Coefficient B |  | -44.103 |  |  | 31.804 | 3495.938 |  |  |  | Temp °R Upstream |  | 519.67 | Data Curve % of Min | Temp °R Upstream |  | 519.67 | Data Curve % of Min |  |  |  |  | Shift Coefficient B |  | 18.369 |  |  | Shift Coefficient B |  | 18.369
| c = | -0.4215 | Specific Gravity |  | 0.6 |  | P Drop (iwc) |  | 83.4231 |  |  | 50.756 | 4450.932 |  |  |  | Specific Gravity |  | 0.6 |  | Specific Gravity |  | 0.6 | [5 empty] | Shift Coefficient C |  | -186.52 |  |  | Shift Coefficient C |  | -186.52
| d = | 0.00201 | Flow Coefficient - Cv |  | 2.7088 | [6 empty] | 71.466 | 5200.014 |  |  |  | Flow Coefficient - Cv |  | 17.5739 | 25.25% | Flow Coefficient - Cv |  | 17.5739 | 31.67% |  |  |  |  | P Drop (psi) |  | 9.3525 |  |  | P Drop (psi) |  | 18.6005
| Max % | 0.5 | P Drop (iwc) |  | 83.8574 |  | Test Data Offset From Min |  | 41.09% |  |  | 94.82 | 6013 |  |  |  | P Drop (psi) |  | 9.3525 |  | P Drop (psi) |  | 18.6005 | [5 empty] | Test Data Offset |  | 25.25% |  |  | Test Data Offset |  | 31.67%
P | Curve Fit Data |  | Cv Calculated Data |  |  |  | Shifted Cv Calculated Data |  |  |  | Test Data Shifted Curve |  |  |  |  | P | 3900 Cv Calculated Data |  |  |  | 5500 Cv Calculated Data |  |  |  | Data from lab test 2012 012 |  |  |  | 3900 Shifted Cv Calculated Data |  |  |  | Test Data Shifted Curve | 5500 Shifted Cv Calculated Data |  |  |  | Test Data Shifted Curve
| Min Trip Point | Max Trip Point | x | Min Trip Flow | Max Trip Flow | Min Trip Flow Difference | x | Shift | Min Trip Flow | Max Trip Flow | [6 empty] | x | Min Trip Flow | Max Trip Flow | Curve at Data | x | Min Trip Flow | Max Trip Flow | Curve at Data |  | CEFV Series 3900 Average of Qualification Data |  |  | X | Shift | Min Trip Flow | Max Trip Flow |  | X | Shift | Min Trip Flow | Max Trip Flow
0 | 1345.4039 | 2018.1058 | 0.20749 | 1386.5032 | 2079.7549 | -41.0993 | 0.20641 | -44.103 | 1338.8053 | 2008.208 | 1888.9859 |  |  |  |  | 0 | 0.023141 | 3004.0903 | 4506.1355 | 3762.6671 | 0.046023 | 4236.5377 | 6354.8065 | 5578.3433 |  | 10 | 60 | 108 | 0.023141 | -186.52 | 2817.5706 | 4226.3559 | 3529.0481 | 0.046023 | -186.52 | 4050.0179 | 6075.0269 | 5072.7063
1 | 1393.8883 | 2090.8325 | 0.19418 | 1433.2313 | 2149.847 | -39.343 | 0.19317 | -39.226 | 1390.2893 | 2085.434 | 1961.6271 |  |  |  |  | 1 | 0.021657 | 3105.3346 | 4658.0019 | 3889.477 | 0.043071 | 4379.318 | 6568.977 | 5766.3454 | 1¼ | 4842.8726 | 9648.8674 | 13057.0502 | 0.021657 | -168.1227 | 2937.2122 | 4405.8183 | 3678.9009 | 0.043071 | -168.1227 | 4211.1956 | 6316.7934 | 5274.5837
2 | 1441.6784 | 2162.5176 | 0.18247 | 1478.4833 | 2217.725 | -36.8049 | 0.18153 | -34.349 | 1440.301 | 2160.4514 | 2032.191 |  |  |  |  | 2 | 0.020351 | 3203.3806 | 4805.0708 | 4012.2811 | 0.040475 | 4517.588 | 6776.382 | 5948.4085 | 2 | 4926.7417 | 8882.4149 | 13089.7519 | 0.020351 | -149.6688 | 3053.7121 | 4580.5681 | 3824.8187 | 0.040475 | -149.6688 | 4367.9195 | 6551.8792 | 5470.8826
3 | 1488.7842 | 2233.1762 | 0.1721 | 1522.3908 | 2283.5863 | -33.6067 | 0.17121 | -29.472 | 1488.9716 | 2233.4574 | 2100.8628 |  |  |  |  | 3 | 0.019194 | 3298.5135 | 4947.7702 | 4131.4364 | 0.038174 | 4651.7498 | 6977.6247 | 6125.0624 | Average | 4884.8071 | 9265.6412 | 13073.4011 | 0.019194 | -131.1583 | 3167.3555 | 4751.0332 | 3967.1588 | 0.038174 | -131.1583 | 4520.5918 | 6780.8877 | 5662.1069
4 | 1535.2157 | 2302.8235 | 0.16284 | 1565.067 | 2347.6005 | -29.8513 | 0.162 | -24.595 | 1536.4141 | 2304.6212 | 2167.8018 |  |  |  |  | 4 | 0.018162 | 3390.9785 | 5086.4678 | 4247.2502 | 0.03612 | 4782.1492 | 7173.2238 | 6296.7622 | Cv Curve Data | 4884.8071 | 8507.6274 | 10906.758 | 0.018162 | -112.5912 | 3278.3876 | 4917.5815 | 4106.2281 | 0.03612 | -112.5912 | 4669.5583 | 7004.3375 | 5848.6896
5 | 1580.9831 | 2371.4746 | 0.15453 | 1606.61 | 2409.915 | -25.6269 | 0.15373 | -19.718 | 1582.7264 | 2374.0896 | 2233.146 |  |  |  |  | 5 | 0.017235 | 3480.9883 | 5221.4824 | 4359.9888 | 0.034277 | 4909.086 | 7363.6291 | 6463.9027 | Difference | 0 | 758.0138 | 2166.6431 | 0.017235 | -93.9675 | 3387.0211 | 5080.5317 | 4242.2931 | 0.034277 | -93.9675 | 4815.1189 | 7222.6783 | 6031.0063
6 | 1626.0964 | 2439.1446 | 0.14703 | 1647.1055 | 2470.6582 | -21.0091 | 0.14626 | -14.841 | 1627.9939 | 2441.9909 | 2297.0162 |  |  |  |  | 6 | 0.016398 | 3568.7286 | 5353.0928 | 4469.8848 | 0.032612 | 5032.8223 | 7549.2335 | 6626.8291 |  |  |  |  | 0.016398 | -75.2872 | 3493.4417 | 5240.1625 | 4375.5865 | 0.032612 | -75.2872 | 4957.5355 | 7436.3032 | 6209.3852
7 | 1670.5657 | 2505.8486 | 0.14022 | 1686.629 | 2529.9435 | -16.0633 | 0.13949 | -9.964 | 1672.2919 | 2508.4379 | 2359.5185 |  |  |  |  | 7 | 0.015638 | 3654.3628 | 5481.5442 | 4577.143 | 0.031101 | 5153.5886 | 7730.3829 | 6785.8447 |  | CEFV Series 5500 Average of Qualification Data |  |  | 0.015638 | -56.5503 | 3597.8129 | 5396.7193 | 4506.3129 | 0.031101 | -56.5503 | 5097.0386 | 7645.558 | 6384.1149
8 | 1714.4012 | 2571.6017 | 0.13401 | 1725.2473 | 2587.8709 | -10.8461 | 0.13331 | -5.087 | 1715.6871 | 2573.5307 | 2420.7468 |  |  |  |  | 8 | 0.014946 | 3738.0358 | 5607.0537 | 4681.9446 | 0.029725 | 5271.589 | 7907.3835 | 6941.2184 |  | 10 | 60 | 105 | 0.014946 | -37.7568 | 3700.2794 | 5550.4191 | 4634.6537 | 0.029725 | -37.7568 | 5233.8325 | 7850.7488 | 6555.4513
9 | 1757.6127 | 2636.4191 | 0.12833 | 1763.0199 | 2644.5298 | -5.4071 | 0.12766 | -0.21 | 1758.2388 | 2637.3582 | 2480.785 |  |  |  |  | 9 | 0.014312 | 3819.8764 | 5729.8146 | 4784.4512 | 0.028465 | 5387.0052 | 8080.5078 | 7093.1896 | 1¼ | 7261.9763 | 14204.8682 | 18795.0538 | 0.014312 | -18.9067 | 3800.9701 | 5701.4551 | 4760.7702 | 0.028465 | -18.9067 | 5368.0989 | 8052.1483 | 6723.6218
10 | 1800.2106 | 2700.3159 | 0.12311 | 1800 | 2700 | 0.21058 | 0.12247 | 4.667 | 1800 | 2700 | 2539.708 |  |  |  |  | 10 | 0.01373 | 3900 | 5850 | 4884.8071 | 0.027307 | 5500 | 8250 | 7241.9723 | 2 | 7221.9683 | 13575.6757 | 17178.1446 | 0.01373 | 0 | 3900.0004 | 5850.0006 | 4884.8071 | 0.027307 | 0 | 5500.0004 | 8250.0006 | 6888.8304
11 | 1842.2047 | 2763.3071 | 0.1183 | 1836.2355 | 2754.3533 | 5.9692 | 0.11769 | 9.544 | 1841.0186 | 2761.5279 | 2597.5831 |  |  |  |  | 11 | 0.013194 | 3978.5103 | 5967.7654 | 4983.1424 | 0.02624 | 5610.7196 | 8416.0795 | 7387.7593 | Average | 7241.9723 | 13890.2719 | 17986.5992 | 0.013194 | 18.9633 | 3997.474 | 5996.211 | 5006.8942 | 0.02624 | 18.9633 | 5629.6833 | 8444.525 | 7051.2601
12 | 1883.6053 | 2825.408 | 0.11385 | 1871.7697 | 2807.6545 | 11.8356 | 0.11326 | 14.421 | 1881.3376 | 2822.0064 | 2654.4712 |  |  |  |  | 12 | 0.012697 | 4055.501 | 6083.2515 | 5079.5744 | 0.025253 | 5719.2963 | 8578.9444 | 7530.7246 | Cv Curve Data | 7241.9723 | 12612.9856 | 15970.7396 | 0.012697 | 37.9832 | 4093.4846 | 6140.2269 | 5127.1489 | 0.025253 | 37.9832 | 5757.2799 | 8635.9198 | 7211.0766
13 | 1924.4223 | 2886.6335 | 0.10972 | 1906.6417 | 2859.9626 | 17.7806 | 0.10915 | 19.298 | 1920.9962 | 2881.4943 | 2710.4275 |  |  |  |  | 13 | 0.012237 | 4131.0571 | 6196.5856 | 5174.2095 | 0.024338 | 5825.8497 | 8738.7745 | 7671.0258 | Difference | 0 | 1277.2863 | 2015.8596 | 0.012237 | 57.0597 | 4188.1171 | 6282.1757 | 5245.6776 | 0.024338 | 57.0597 | 5882.9098 | 8824.3647 | 7368.43
14 | 1964.6659 | 2946.9989 | 0.10588 | 1940.8873 | 2911.331 | 23.7786 | 0.10534 | 24.175 | 1960.03 | 2940.045 | 2765.5022 |  |  |  |  | 14 | 0.011809 | 4205.2558 | 6307.8837 | 5267.1445 | 0.023486 | 5930.489 | 8895.7335 | 7808.8067 |  |  |  |  | 0.011809 | 76.1928 | 4281.449 | 6422.1735 | 5362.5771 | 0.023486 | 76.1928 | 6006.6822 | 9010.0233 | 7523.4567
15 | 2004.3462 | 3006.5193 | 0.10231 | 1974.539 | 2961.8085 | 29.8071 | 0.10178 | 29.052 | 1998.4715 | 2997.7073 | 2819.7411 |  |  |  |  | 15 | 0.01141 | 4278.1679 | 6417.2519 | 5358.468 | 0.022693 | 6033.3137 | 9049.9706 | 7944.1983 |  | Pressure | Ave Diff Flow |  | 0.01141 | 95.3825 | 4373.5508 | 6560.3262 | 5477.9359 | 0.022693 | 95.3825 | 6128.6966 | 9193.0449 | 7676.2815
16 | 2043.4731 | 3065.2097 | 0.098962 | 2007.6268 | 3011.4402 | 35.8463 | 0.09845 | 33.929 | 2036.3505 | 3054.5257 | 2873.1864 |  |  |  |  | 16 | 0.011037 | 4349.858 | 6524.787 | 5448.2609 | 0.021951 | 6134.4152 | 9201.6227 | 8077.3208 |  |  |  |  | 0.011037 | 114.6288 | 4464.4872 | 6696.7308 | 5591.8351 | 0.021951 | 114.6288 | 6249.0444 | 9373.5665 | 7827.0188
17 | 2082.0568 | 3123.0853 | 0.095829 | 2040.178 | 3060.267 | 41.8789 | 0.095333 | 38.806 | 2073.6943 | 3110.5414 | 2925.8766 |  |  |  |  | 17 | 0.010688 | 4420.3856 | 6630.5784 | 5536.5977 | 0.021256 | 6233.8771 | 9350.8157 | 8208.2847 |  | 10 | 0 |  | 0.010688 | 133.9317 | 4554.3177 | 6831.4766 | 5704.3491 | 0.021256 | 133.9317 | 6367.8093 | 9551.7139 | 7975.7736
18 | 2120.1075 | 3180.1612 | 0.092889 | 2072.2179 | 3108.3269 | 47.8896 | 0.092408 | 43.683 | 2110.5281 | 3165.7922 | 2977.8473 |  |  |  |  | 18 | 0.01036 | 4489.8055 | 6734.7082 | 5623.5471 | 0.020604 | 6331.7769 | 9497.6654 | 8337.1915 |  | 60 | 1017.6501 |  | 0.01036 | 153.2912 | 4643.0971 | 6964.6456 | 5815.5465 | 0.020604 | 153.2912 | 6485.0685 | 9727.6028 | 8122.6426
19 | 2157.635 | 3236.4525 | 0.090124 | 2103.7699 | 3155.6549 | 53.8651 | 0.089657 | 48.56 | 2146.8753 | 3220.313 | 3029.1313 |  |  |  |  | 19 | 0.010051 | 4558.1682 | 6837.2523 | 5709.1724 | 0.01999 | 6428.1859 | 9642.2788 | 8464.1353 |  | 106.5 | 2091.2513 |  | 0.010051 | 172.7073 | 4730.8759 | 7096.3139 | 5925.4908 | 0.01999 | 172.7073 | 6600.8936 | 9901.3404 | 8267.7152
20 | 2194.6496 | 3291.9744 | 0.087518 | 2134.8557 | 3202.2835 | 59.7939 | 0.087065 | 53.437 | 2182.7575 | 3274.1362 | 3079.7592 |  |  |  |  | 20 | 0.0097608 | 4625.5207 | 6938.281 | 5793.5324 | 0.019413 | 6523.1701 | 9784.7552 | 8589.2032 |  |  |  |  | 0.0097608 | 192.18 | 4817.7011 | 7226.5516 | 6034.2406 | 0.019413 | 192.18 | 6715.3506 | 10073.0259 | 8411.0742
21 | 2231.1613 | 3346.7419 | 0.085059 | 2165.4952 | 3248.2429 | 65.666 | 0.084619 | 58.314 | 2218.1946 | 3327.2919 | 3129.7592 |  |  |  |  | 21 | 0.0094865 | 4691.9064 | 7037.8596 | 5876.6814 | 0.018867 | 6616.791 | 9925.1866 | 8712.4759 |  |  |  |  | 0.0094866 | 211.7093 | 4903.6161 | 7355.4242 | 6141.8504 | 0.018867 | 211.7093 | 6828.5008 | 10242.7512 | 8552.7964
22 | 2267.1801 | 3400.7702 | 0.082734 | 2195.7073 | 3293.5609 | 71.4728 | 0.082306 | 63.191 | 2253.2053 | 3379.808 | 3179.1575 |  |  |  |  | 22 | 0.0092273 | 4757.3658 | 7136.0487 | 5958.6704 | 0.018351 | 6709.1056 | 10063.6585 | 8834.0286 |  |  |  |  | 0.0092273 | 231.2952 | 4988.6615 | 7482.9922 | 6248.371 | 0.018351 | 231.2952 | 6940.4013 | 10410.6019 | 8692.9534
23 | 2302.7162 | 3454.0744 | 0.080533 | 2225.5092 | 3338.2639 | 77.207 | 0.080116 | 68.068 | 2287.807 | 3431.7105 | 3227.9787 |  |  |  |  | 23 | 0.0089818 | 4821.9367 | 7232.9051 | 6039.5463 | 0.017863 | 6800.1672 | 10200.2507 | 8953.9313 |  |  |  |  | 0.0089818 | 250.9377 | 5072.8749 | 7609.3123 | 6353.8495 | 0.017863 | 250.9377 | 7051.1053 | 10576.658 | 8831.6118
24 | 2337.7797 | 3506.6695 | 0.078447 | 2254.9174 | 3382.376 | 82.8623 | 0.07804 | 72.945 | 2322.0159 | 3483.0238 | 3276.2457 |  |  |  |  | 24 | 0.0087491 | 4885.6543 | 7328.4814 | 6119.3535 | 0.0174 | 6890.0253 | 10335.0379 | 9072.2495 |  |  |  |  | 0.0087491 | 270.6368 | 5156.2915 | 7734.4373 | 6458.3301 | 0.0174 | 270.6368 | 7160.6625 | 10740.9938 | 8968.8338
25 | 2372.3806 | 3558.5709 | 0.076465 | 2283.9468 | 3425.9203 | 88.4337 | 0.076069 | 77.822 | 2355.8471 | 3533.7706 | 3323.9798 |  |  |  |  | 25 | 0.0085281 | 4948.5515 | 7422.8272 | 6198.1332 | 0.016961 | 6978.7265 | 10468.0897 | 9189.0443 |  |  |  |  | 0.0085281 | 290.3925 | 5238.9445 | 7858.4167 | 6561.854 | 0.016961 | 290.3925 | 7269.1194 | 10903.6792 | 9104.6777
26 | 2406.5289 | 3609.7934 | 0.074581 | 2312.612 | 3468.9179 | 93.917 | 0.074195 | 82.699 | 2389.3149 | 3583.9723 | 3371.2012 |  |  |  |  | 26 | 0.008318 | 5010.6592 | 7515.9889 | 6275.9241 | 0.016543 | 7066.3143 | 10599.4715 | 9304.3732 |  |  |  |  | 0.008318 | 310.2048 | 5320.8645 | 7981.2968 | 6664.4601 | 0.016543 | 310.2048 | 7376.5196 | 11064.7794 | 9239.1979
27 | 2440.2349 | 3660.3523 | 0.072788 | 2340.9261 | 3511.3891 | 99.3088 | 0.072411 | 87.576 | 2422.4326 | 3633.6489 | 3417.9286 |  |  |  |  | 27 | 0.008118 | 5072.0065 | 7608.0098 | 6352.7624 | 0.016145 | 7152.8297 | 10729.2446 | 9418.2899 |  |  |  |  | 0.008118 | 330.0737 | 5402.0807 | 8103.1211 | 6766.1846 | 0.016145 | 330.0737 | 7482.9039 | 11224.3558 | 9372.4458
28 | 2473.5085 | 3710.2627 | 0.071079 | 2368.9018 | 3553.3527 | 104.6066 | 0.070711 | 92.453 | 2455.2128 | 3682.8192 | 3464.1797 |  |  |  |  | 28 | 0.0079274 | 5132.6206 | 7698.9309 | 6428.6825 | 0.015766 | 7238.3111 | 10857.4667 | 9530.8452 |  |  |  |  | 0.0079274 | 349.9992 | 5482.6203 | 8223.9304 | 6867.0616 | 0.015766 | 349.9992 | 7588.3108 | 11382.4662 | 9504.4695
29 | 2506.3598 | 3759.5397 | 0.069448 | 2396.551 | 3594.8265 | 109.8088 | 0.069089 | 97.33 | 2487.6673 | 3731.5009 | 3509.9714 |  |  |  |  | 29 | 0.0077455 | 5192.5272 | 7788.7908 | 6503.7163 | 0.015404 | 7322.7947 | 10984.1921 | 9642.0867 |  |  |  |  | 0.0077455 | 369.9813 | 5562.509 | 8343.7634 | 6967.1233 | 0.015404 | 369.9813 | 7692.7765 | 11539.1648 | 9635.3143
30 | 2538.7989 | 3808.1983 | 0.067891 | 2423.8848 | 3635.8272 | 114.9141 | 0.067539 | 102.207 | 2519.8072 | 3779.7108 | 3555.3192 |  |  |  |  | 30 | 0.0075718 | 5251.7504 | 7877.6256 | 6577.8943 | 0.015059 | 7406.3147 | 11109.4721 | 9752.0593 |  |  |  |  | 0.0075718 | 390.02 | 5641.7709 | 8462.6564 | 7066.4 | 0.015059 | 390.02 | 7796.3352 | 11694.5028 | 9765.0231
31 | 2570.8359 | 3856.2538 | 0.066402 | 2450.9138 | 3676.3707 | 119.9221 | 0.066058 | 107.084 | 2551.6431 | 3827.4647 | 3600.238 |  |  |  |  | 31 | 0.0074057 | 5310.3132 | 7965.4699 | 6651.2451 | 0.014729 | 7488.9033 | 11233.3549 | 9860.8055 |  |  |  |  | 0.0074057 | 410.1153 | 5720.429 | 8580.6436 | 7164.9205 | 0.014729 | 410.1153 | 7899.0191 | 11848.5286 | 9893.6361
32 | 2602.4808 | 3903.7213 | 0.064976 | 2477.6479 | 3716.4719 | 124.8329 | 0.06464 | 111.961 | 2583.185 | 3874.7774 | 3644.7419 |  |  |  |  | 32 | 0.0072468 | 5368.2372 | 8052.3558 | 6723.7957 | 0.014413 | 7570.5909 | 11355.8864 | 9968.3654 |  |  |  |  | 0.0072468 | 430.2672 | 5798.5049 | 8697.7574 | 7262.7116 | 0.014413 | 430.2672 | 8000.8586 | 12001.288 | 10021.1917
33 | 2633.7438 | 3950.6158 | 0.063611 | 2504.0967 | 3756.145 | 129.6472 | 0.063282 | 116.838 | 2614.4421 | 3921.6632 | 3688.8442 |  |  |  |  | 33 | 0.0070945 | 5425.5428 | 8138.3142 | 6795.5718 | 0.01411 | 7651.4065 | 11477.1098 | 10074.7771 |  |  |  |  | 0.0070945 | 450.4757 | 5876.019 | 8814.0286 | 7359.7992 | 0.01411 | 450.4757 | 8101.8828 | 12152.8241 | 10147.7258
34 | 2664.635 | 3996.9524 | 0.062302 | 2530.269 | 3795.4035 | 134.366 | 0.061979 | 121.715 | 2645.4236 | 3968.1353 | 3732.5574 |  |  |  |  | 34 | 0.0069485 | 5482.2495 | 8223.3742 | 6866.5977 | 0.013819 | 7731.3774 | 11597.0661 | 10180.0766 |  |  |  |  | 0.0069485 | 470.7408 | 5952.9908 | 8929.4862 | 7456.2074 | 0.013819 | 470.7408 | 8202.1187 | 12303.1781 | 10273.2729
35 | 2695.1643 | 4042.7464 | 0.061046 | 2556.1733 | 3834.26 | 138.991 | 0.060729 | 126.592 | 2676.1377 | 4014.2066 | 3775.8935 |  |  |  |  | 35 | 0.0068084 | 5538.3755 | 8307.5633 | 6936.8964 | 0.013541 | 7810.5295 | 11715.7943 | 10284.2979 |  |  |  |  | 0.0068084 | 491.0625 | 6029.4385 | 9044.1578 | 7551.9593 | 0.013541 | 491.0625 | 8301.5926 | 12452.3889 | 10397.8653
36 | 2725.3419 | 4088.0128 | 0.059839 | 2581.8177 | 3872.7266 | 143.5241 | 0.059529 | 131.469 | 2706.5927 | 4059.889 | 3818.8639 |  |  |  |  | 36 | 0.0066738 | 5593.9384 | 8390.9077 | 7006.4898 | 0.013273 | 7888.8875 | 11833.3313 | 10387.4737 |  |  |  |  | 0.0066738 | 511.4408 | 6105.3798 | 9158.0697 | 7647.0769 | 0.013273 | 511.4408 | 8400.3289 | 12600.4933 | 10521.5339
37 | 2755.1778 | 4132.7667 | 0.058679 | 2607.2099 | 3910.8149 | 147.9678 | 0.058375 | 136.346 | 2736.796 | 4105.1941 | 3861.4793 |  |  |  |  | 37 | 0.0065444 | 5648.9549 | 8473.4323 | 7075.3987 | 0.013016 | 7966.4749 | 11949.7123 | 10489.6346 |  |  |  |  | 0.0065444 | 531.8757 | 6180.8311 | 9271.2467 | 7741.5808 | 0.013016 | 531.8757 | 8498.3511 | 12747.5266 | 10644.3082
38 | 2784.6822 | 4177.0232 | 0.057563 | 2632.3572 | 3948.5358 | 152.3249 | 0.057265 | 141.223 | 2766.7551 | 4150.1327 | 3903.7501 |  |  |  |  | 38 | 0.00642 | 5703.4407 | 8555.161 | 7143.643 | 0.012768 | 8043.3138 | 12064.9707 | 10590.8101 |  |  |  |  | 0.00642 | 552.3672 | 6255.8084 | 9383.7126 | 7835.4909 | 0.012768 | 552.3672 | 8595.6815 | 12893.5223 | 10766.216
39 | 2813.865 | 4220.7976 | 0.056489 | 2657.2665 | 3985.8998 | 156.5985 | 0.056197 | 146.1 | 2796.4769 | 4194.7153 | 3945.6859 |  |  |  |  | 39 | 0.0063002 | 5757.4108 | 8636.1163 | 7211.2414 | 0.01253 | 8119.4256 | 12179.1383 | 10691.0282 |  |  |  |  | 0.0063002 | 572.9153 | 6330.3267 | 9495.49 | 7928.8261 | 0.01253 | 572.9153 | 8692.3414 | 13038.5121 | 10887.2839
40 | 2842.7365 | 4264.1047 | 0.055454 | 2681.9445 | 4022.9168 | 160.792 | 0.055167 | 150.977 | 2825.9678 | 4238.9518 | 3987.2962 |  |  |  |  | 40 | 0.0061848 | 5810.8798 | 8716.3197 | 7278.212 | 0.0123 | 8194.8305 | 12292.2457 | 10790.3155 |  |  |  |  | 0.0061848 | 593.52 | 6404.4003 | 9606.6005 | 8021.6044 | 0.0123 | 593.52 | 8788.351 | 13182.5265 | 11007.5373
41 | 2871.3066 | 4306.9599 | 0.054457 | 2706.3975 | 4059.5962 | 164.9091 | 0.054175 | 155.854 | 2855.2344 | 4282.8516 | 4028.5898 |  |  |  |  | 41 | 0.0060735 | 5863.8612 | 8795.7918 | 7344.572 | 0.012079 | 8269.5478 | 12404.3217 | 10888.6975 |  |  |  |  | 0.0060735 | 614.1813 | 6478.043 | 9717.0645 | 8113.843 | 0.012079 | 614.1813 | 8883.7297 | 13325.5945 | 11127.0005
42 | 2899.5855 | 4349.3782 | 0.053494 | 2730.6314 | 4095.9472 | 168.954 | 0.053217 | 160.731 | 2884.2825 | 4326.4238 | 4069.5752 |  |  |  |  | 42 | 0.0059662 | 5916.3681 | 8874.5522 | 7410.3377 | 0.011866 | 8343.5961 | 12515.3942 | 10986.1985 |  |  |  |  | 0.0059662 | 634.8992 | 6551.2679 | 9826.9019 | 8205.5582 | 0.011866 | 634.8992 | 8978.4959 | 13467.7438 | 11245.6965
43 | 2927.5832 | 4391.3747 | 0.052566 | 2754.6522 | 4131.9784 | 172.9309 | 0.052293 | 165.608 | 2913.1181 | 4369.6771 | 4110.2607 |  |  |  |  | 43 | 0.0058626 | 5968.4132 | 8952.6198 | 7475.5249 | 0.01166 | 8416.993 | 12625.4895 | 11082.8418 |  |  |  |  | 0.0058626 | 655.6737 | 6624.0875 | 9936.1312 | 8296.7658 | 0.01166 | 655.6737 | 9072.6672 | 13609.0009 | 11363.6475
44 | 2955.3097 | 4432.9646 | 0.051668 | 2778.4654 | 4167.6981 | 176.8443 | 0.051401 | 170.485 | 2941.7464 | 4412.6197 | 4150.6539 |  |  |  |  | 44 | 0.0057625 | 6020.0083 | 9030.0125 | 7540.1486 | 0.011461 | 8489.7553 | 12734.633 | 11178.6496 |  |  |  |  | 0.0057625 | 676.5048 | 6696.5137 | 10044.7705 | 8387.4807 | 0.011461 | 676.5048 | 9166.2607 | 13749.3911 | 11480.8747
45 | 2982.7753 | 4474.1629 | 0.050801 | 2802.0761 | 4203.1142 | 180.6991 | 0.050538 | 175.362 | 2970.173 | 4455.2595 | 4190.7623 |  |  |  |  | 45 | 0.0056658 | 6071.165 | 9106.7475 | 7604.2231 | 0.011268 | 8561.8994 | 12842.849 | 11273.6433 |  |  |  |  | 0.0056658 | 697.3925 | 6768.5581 | 10152.8371 | 8477.7173 | 0.011268 | 697.3925 | 9259.2924 | 13888.9386 | 11597.3983
46 | 3009.9899 | 4514.9848 | 0.049963 | 2825.4896 | 4238.2344 | 184.5003 | 0.049704 | 180.239 | 2998.4028 | 4497.6042 | 4230.593 |  |  |  |  | 46 | 0.0055723 | 6121.8942 | 9182.8413 | 7667.7621 | 0.011082 | 8633.4405 | 12950.1608 | 11367.8431 |  |  |  |  | 0.0055723 | 718.3368 | 6840.2316 | 10260.3474 | 8567.4894 | 0.011082 | 718.3368 | 9351.7779 | 14027.6669 | 11713.2377
47 | 3036.9636 | 4555.4454 | 0.049152 | 2848.7107 | 4273.066 | 188.2529 | 0.048897 | 185.116 | 3026.4406 | 4539.6609 | 4270.153 |  |  |  |  | 47 | 0.0054818 | 6172.2065 | 9258.3097 | 7730.779 | 0.010902 | 8704.3937 | 13056.5906 | 11461.2688 |  |  |  |  | 0.0054818 | 739.3377 | 6911.5447 | 10367.3171 | 8656.8102 | 0.010902 | 739.3377 | 9443.732 | 14165.598 | 11828.4115
48 | 3063.7066 | 4595.5598 | 0.048366 | 2871.744 | 4307.6159 | 191.9626 | 0.048116 | 189.993 | 3054.2912 | 4581.4368 | 4309.4487 |  |  |  |  | 48 | 0.0053943 | 6222.1119 | 9333.1679 | 7793.2863 | 0.010728 | 8774.7732 | 13162.1598 | 11553.939 |  |  |  |  | 0.0053943 | 760.3952 | 6982.5077 | 10473.7616 | 8745.6923 | 0.010728 | 760.3952 | 9535.169 | 14302.7535 | 11942.9377
49 | 3090.2288 | 4635.3432 | 0.047606 | 2894.594 | 4341.891 | 195.6348 | 0.047359 | 194.87 | 3081.9589 | 4622.9384 | 4348.4865 |  |  |  |  | 49 | 0.0053094 | 6271.6203 | 9407.4304 | 7855.2962 | 0.01056 | 8844.5927 | 13266.8891 | 11645.8719 |  |  |  |  | 0.0053094 | 781.5093 | 7053.1302 | 10579.6953 | 8834.148 | 0.01056 | 781.5093 | 9626.1026 | 14439.1539 | 12056.8333
50 | 3116.5404 | 4674.8106 | 0.046869 | 2917.265 | 4375.8975 | 199.2754 | 0.046626 | 199.747 | 3109.4482 | 4664.1723 | 4387.2725 |  |  |  |  | 50 | 0.0052272 | 6320.7409 | 9481.1113 | 7916.8205 | 0.010396 | 8913.8653 | 13370.798 | 11737.0847 |  |  |  |  | 0.0052272 | 802.68 | 7123.4215 | 10685.1322 | 8922.1889 | 0.010396 | 802.68 | 9716.5459 | 14574.8189 | 12170.1149
51 | 3142.6514 | 4713.9771 | 0.046154 | 2939.7612 | 4409.6418 | 202.8902 | 0.045915 | 204.624 | 3136.7631 | 4705.1446 | 4425.8124 |  |  |  |  | 51 | 0.0051475 | 6369.4826 | 9554.224 | 7977.8703 | 0.010238 | 8982.6037 | 13473.9056 | 11827.5941 |  |  |  |  | 0.0051475 | 823.9073 | 7193.3905 | 10790.0858 | 9009.8262 | 0.010238 | 823.9073 | 9806.5116 | 14709.7674 | 12282.7983
52 | 3168.572 | 4752.858 | 0.045461 | 2962.0866 | 4443.1299 | 206.4854 | 0.045226 | 209.501 | 3163.9076 | 4745.8613 | 4464.1118 |  |  |  |  | 52 | 0.0050702 | 6417.8543 | 9626.7814 | 8038.4564 | 0.010084 | 9050.8201 | 13576.2302 | 11917.4161 |  |  |  |  | 0.0050702 | 845.1912 | 7263.0461 | 10894.5691 | 9097.0707 | 0.010084 | 845.1912 | 9896.0119 | 14844.0179 | 12394.8987
53 | 3194.3121 | 4791.4682 | 0.044788 | 2984.2449 | 4476.3674 | 210.0672 | 0.044556 | 214.378 | 3190.8855 | 4786.3282 | 4502.1763 |  |  |  |  | 53 | 0.0049952 | 6465.864 | 9698.796 | 8098.5894 | 0.0099346 | 9118.5262 | 13677.7893 | 12006.5662 |  |  |  |  | 0.0049952 | 866.5317 | 7332.3963 | 10998.5945 | 9183.9329 | 0.0099346 | 866.5317 | 9985.0585 | 14977.5877 | 12506.4308
54 | 3219.882 | 4829.823 | 0.044135 | 3006.24 | 4509.3599 | 213.642 | 0.043907 | 219.255 | 3217.7005 | 4826.5507 | 4540.0109 |  |  |  |  | 54 | 0.0049224 | 6513.5199 | 9770.2799 | 8158.2791 | 0.0097897 | 9185.7332 | 13778.5998 | 12095.0592 |  |  |  |  | 0.0049224 | 887.9288 | 7401.4493 | 11102.174 | 9270.4228 | 0.0097898 | 887.9288 | 10073.6626 | 15110.4939 | 12617.4088
55 | 3245.2916 | 4867.9374 | 0.043501 | 3028.0752 | 4542.1128 | 217.2164 | 0.043276 | 224.132 | 3244.3561 | 4866.5342 | 4577.6206 |  |  |  |  | 55 | 0.0048516 | 6560.8297 | 9841.2445 | 8217.5352 | 0.0096491 | 9252.4521 | 13878.6781 | 12182.9094 |  |  |  |  | 0.0048517 | 909.3825 | 7470.2128 | 11205.3192 | 9356.55 | 0.0096491 | 909.3825 | 10161.8352 | 15242.7528 | 12727.8462
56 | 3270.551 | 4905.8265 | 0.042885 | 3049.7542 | 4574.6312 | 220.7968 | 0.042663 | 229.009 | 3270.8558 | 4906.2838 | 4615.0104 |  |  |  |  | 56 | 0.0047829 | 6607.8007 | 9911.701 | 8276.3671 | 0.0095124 | 9318.6933 | 13978.0399 | 12270.1306 |  |  |  |  | 0.0047829 | 930.8928 | 7538.6941 | 11308.0412 | 9442.3239 | 0.0095124 | 930.8928 | 10249.5867 | 15374.38 | 12837.7562
57 | 3295.6703 | 4943.5055 | 0.042286 | 3071.2801 | 4606.9201 | 224.3903 | 0.042067 | 233.886 | 3297.2029 | 4945.8044 | 4652.1848 |  |  |  |  | 57 | 0.0047161 | 6654.4402 | 9981.6603 | 8334.7838 | 0.0093795 | 9384.4669 | 14076.7004 | 12356.7363 |  |  |  |  | 0.0047161 | 952.4597 | 7606.9005 | 11410.3507 | 9527.7534 | 0.0093795 | 952.4597 | 10336.9272 | 15505.3908 | 12947.1515
58 | 3320.6597 | 4980.9895 | 0.041703 | 3092.6562 | 4638.9842 | 228.0035 | 0.041487 | 238.763 | 3323.4006 | 4985.1009 | 4689.1484 |  |  |  |  | 58 | 0.0046511 | 6700.755 | 10051.1326 | 8392.7938 | 0.0092503 | 9449.7827 | 14174.6741 | 12442.7391 |  |  |  |  | 0.0046511 | 974.0832 | 7674.8389 | 11512.2583 | 9612.8472 | 0.0092503 | 974.0832 | 10423.8666 | 15635.7999 | 13056.0443
59 | 3345.529 | 5018.2936 | 0.041137 | 3113.8855 | 4670.8283 | 231.6435 | 0.040924 | 243.64 | 3349.4519 | 5024.1779 | 4725.9054 |  |  |  |  | 59 | 0.0045879 | 6746.752 | 10120.128 | 8450.4056 | 0.0091246 | 9514.6502 | 14271.9753 | 12528.1515 |  |  |  |  | 0.0045879 | 995.7633 | 7742.5159 | 11613.7739 | 9697.6136 | 0.0091246 | 995.7633 | 10510.4142 | 15765.6212 | 13164.4464
60 | 3370.2886 | 5055.4329 | 0.040585 | 3134.9711 | 4702.4567 | 235.3175 | 0.040375 | 248.517 | 3375.3598 | 5063.0398 | 4762.4602 |  |  |  |  | 60 | 0.0045264 | 6792.4374 | 10188.6562 | 8507.6274 | 0.0090023 | 9579.0784 | 14368.6176 | 12612.9856 |  |  |  |  | 0.0045264 | 1017.5 | 7809.9381 | 11714.9071 | 9782.0609 | 0.0090023 | 1017.5 | 10596.5791 | 15894.8686 | 13272.3692
61 | 3394.9483 | 5092.4225 | 0.040048 | 3155.9158 | 4733.8738 | 239.0325 | 0.039841 | 253.394 | 3401.1273 | 5101.6909 | 4798.8167 |  |  |  |  | 61 | 0.0044665 | 6837.8177 | 10256.7265 | 8564.4668 | 0.0088832 | 9643.0762 | 14464.6143 | 12697.2529 |  |  |  |  | 0.0044665 | 1039.2933 | 7877.1116 | 11815.6674 | 9866.1967 | 0.0088832 | 1039.2933 | 10682.3701 | 16023.5552 | 13379.8238
62 | 3419.5184 | 5129.2776 | 0.039525 | 3176.7225 | 4765.0837 | 242.7959 | 0.039321 | 258.271 | 3426.757 | 5140.1354 | 4834.9789 |  |  |  |  | 62 | 0.0044082 | 6882.8987 | 10324.3481 | 8620.9314 | 0.0087672 | 9706.652 | 14559.978 | 12780.9646 |  |  |  |  | 0.0044082 | 1061.1432 | 7944.0426 | 11916.0638 | 9950.0287 | 0.0087672 | 1061.1432 | 10767.7959 | 16151.6938 | 13486.8207
63 | 3444.0088 | 5166.0132 | 0.039016 | 3197.3937 | 4796.0906 | 246.6151 | 0.038814 | 263.148 | 3452.2516 | 5178.3774 | 4870.9505 |  |  |  |  | 63 | 0.0043514 | 6927.6864 | 10391.5296 | 8677.0287 | 0.0086542 | 9769.8141 | 14654.7212 | 12864.1315 |  |  |  |  | 0.0043514 | 1083.0497 | 8010.7367 | 12016.1051 | 10033.5641 | 0.0086542 | 1083.0497 | 10852.8645 | 16279.2967 | 13593.3704
64 | 3468.4297 | 5202.6446 | 0.03852 | 3217.9322 | 4826.8983 | 250.4976 | 0.03832 | 268.025 | 3477.6138 | 5216.4207 | 4906.7353 |  |  |  |  | 64 | 0.004296 | 6972.1864 | 10458.2796 | 8732.7655 | 0.0085441 | 9832.5705 | 14748.8558 | 12946.7643 |  |  |  |  | 0.004296 | 1105.0128 | 8077.1998 | 12115.7997 | 10116.8101 | 0.0085441 | 1105.0128 | 10937.584 | 16406.376 | 13699.4828
65 | 3492.7912 | 5239.1867 | 0.038036 | 3238.3404 | 4857.5105 | 254.4508 | 0.037839 | 272.902 | 3502.8461 | 5254.2691 | 4942.3368 |  |  |  |  | 65 | 0.0042421 | 7016.4041 | 10524.6062 | 8788.1489 | 0.0084367 | 9894.9289 | 14842.3934 | 13028.8729 |  |  |  |  | 0.0042421 | 1127.0325 | 8143.4373 | 12215.1559 | 10199.7735 | 0.0084367 | 1127.0325 | 11021.9621 | 16532.9431 | 13805.1676
66 | 3517.1032 | 5275.6548 | 0.037564 | 3258.6207 | 4887.9311 | 258.4824 | 0.037369 | 277.779 | 3527.9509 | 5291.9263 | 4977.7584 |  |  |  |  | 66 | 0.0041894 | 7060.345 | 10590.5175 | 8843.1855 | 0.008332 | 9956.8967 | 14935.3451 | 13110.4674 |  |  |  |  | 0.0041894 | 1149.1088 | 8209.4544 | 12314.1816 | 10282.4609 | 0.008332 | 1149.1088 | 11106.0062 | 16659.0093 | 13910.4341
67 | 3541.3759 | 5312.0639 | 0.037103 | 3278.7757 | 4918.1635 | 262.6002 | 0.036911 | 282.656 | 3552.9306 | 5329.3959 | 5013.0034 |  |  |  |  | 67 | 0.0041381 | 7104.014 | 10656.021 | 8897.8816 | 0.0082299 | 10018.4813 | 15027.722 | 13191.5571 |  |  |  |  | 0.0041381 | 1171.2417 | 8275.2564 | 12412.8846 | 10364.8788 | 0.0082299 | 1171.2417 | 11189.7237 | 16784.5855 | 14015.2915
68 | 3565.6194 | 5348.4291 | 0.036654 | 3298.8075 | 4948.2113 | 266.8119 | 0.036464 | 287.533 | 3577.7874 | 5366.6812 | 5048.0752 |  |  |  |  | 68 | 0.004088 | 7147.4163 | 10721.1244 | 8952.2435 | 0.0081303 | 10079.6896 | 15119.5344 | 13272.1514 |  |  |  |  | 0.004088 | 1193.4312 | 8340.8481 | 12511.2722 | 10447.0335 | 0.0081303 | 1193.4312 | 11273.1215 | 16909.6822 | 14119.7484
69 | 3589.8438 | 5384.7657 | 0.036215 | 3318.7184 | 4978.0776 | 271.1254 | 0.036028 | 292.41 | 3602.5237 | 5403.7856 | 5082.9768 |  |  |  |  | 69 | 0.0040391 | 7190.5565 | 10785.8348 | 9006.2774 | 0.008033 | 10140.5285 | 15210.7927 | 13352.2593 |  |  |  |  | 0.0040391 | 1215.6773 | 8406.2345 | 12609.3518 | 10528.9309 | 0.008033 | 1215.6773 | 11356.2064 | 17034.3097 | 14223.8135
70 | 3614.0591 | 5421.0886 | 0.035787 | 3338.5106 | 5007.7658 | 275.5485 | 0.035602 | 297.287 | 3627.1416 | 5440.7123 | 5117.7113 |  |  |  |  | 70 | 0.0039913 | 7233.4395 | 10850.1593 | 9059.989 | 0.007938 | 10201.0045 | 15301.5067 | 13431.8894 |  |  |  |  | 0.0039913 | 1237.98 | 8471.4202 | 12707.1303 | 10610.5769 | 0.007938 | 1237.98 | 11438.9852 | 17158.4777 | 14327.4951
71 | 3638.2753 | 5457.413 | 0.035369 | 3358.1861 | 5037.2791 | 280.0893 | 0.035186 | 302.164 | 3651.643 | 5477.4646 | 5152.2817 |  |  |  |  | 71 | 0.0039447 | 7276.0698 | 10914.1047 | 9113.384 | 0.0078453 | 10261.1241 | 15391.6861 | 13511.0502 |  |  |  |  | 0.0039447 | 1260.3393 | 8536.4098 | 12804.6147 | 10691.9773 | 0.0078453 | 1260.3393 | 11521.4641 | 17282.1961 | 14430.8011
72 | 3662.5027 | 5493.754 | 0.034961 | 3377.747 | 5066.6204 | 284.7557 | 0.03478 | 307.041 | 3676.0302 | 5514.0453 | 5186.6907 |  |  |  |  | 72 | 0.0038991 | 7318.4517 | 10977.6776 | 9166.468 | 0.0077547 | 10320.8935 | 15481.3402 | 13589.7499 |  |  |  |  | 0.0038991 | 1282.7552 | 8601.2076 | 12901.8114 | 10773.1375 | 0.0077547 | 1282.7552 | 11603.6494 | 17405.474 | 14533.7394
73 | 3686.7512 | 5530.1268 | 0.034562 | 3397.1952 | 5095.7928 | 289.556 | 0.034383 | 311.918 | 3700.3051 | 5550.4576 | 5220.9413 |  |  |  |  | 73 | 0.0038546 | 7360.5896 | 11040.8845 | 9219.2463 | 0.0076662 | 10380.3187 | 15570.4781 | 13667.9965 |  |  |  |  | 0.0038546 | 1305.2277 | 8665.818 | 12998.7271 | 10854.063 | 0.0076662 | 1305.2277 | 11685.5471 | 17528.3207 | 14636.3175
74 | 3711.031 | 5566.5464 | 0.034171 | 3416.5328 | 5124.7992 | 294.4982 | 0.033995 | 316.795 | 3724.4695 | 5586.7042 | 5255.0361 |  |  |  |  | 74 | 0.0038111 | 7402.4877 | 11103.7315 | 9271.7242 | 0.0075796 | 10439.4057 | 15659.1086 | 13745.7977 |  |  |  |  | 0.0038111 | 1327.7568 | 8730.2452 | 13095.3678 | 10934.7589 | 0.0075796 | 1327.7568 | 11767.1632 | 17650.7448 | 14738.5429
75 | 3735.352 | 5603.028 | 0.03379 | 3435.7615 | 5153.6423 | 299.5905 | 0.033615 | 321.672 | 3748.5254 | 5622.788 | 5288.9777 |  |  |  |  | 75 | 0.0037686 | 7444.1499 | 11166.2249 | 9323.9068 | 0.007495 | 10498.1602 | 15747.2402 | 13823.1609 |  |  |  |  | 0.0037686 | 1350.3425 | 8794.4931 | 13191.7397 | 11015.2304 | 0.007495 | 1350.3425 | 11848.5034 | 17772.755 | 14840.4226
76 | 3759.7245 | 5639.5867 | 0.033417 | 3454.8832 | 5182.3248 | 304.8413 | 0.033244 | 326.549 | 3772.4745 | 5658.7117 | 5322.7686 |  |  |  |  | 76 | 0.003727 | 7485.5803 | 11228.3704 | 9375.7989 | 0.0074123 | 10556.5876 | 15834.8814 | 13900.0936 |  |  |  |  | 0.003727 | 1372.9848 | 8858.5658 | 13287.8487 | 11095.4823 | 0.0074123 | 1372.9848 | 11929.5731 | 17894.3596 | 14941.9636
77 | 3784.1584 | 5676.2376 | 0.033052 | 3473.8997 | 5210.8495 | 310.2587 | 0.032881 | 331.426 | 3796.3186 | 5694.4779 | 5356.4115 |  |  |  |  | 77 | 0.0036863 | 7526.7826 | 11290.1739 | 9427.4054 | 0.0073314 | 10614.6934 | 15922.0401 | 13976.6029 |  |  |  |  | 0.0036863 | 1395.6837 | 8922.467 | 13383.7005 | 11175.5196 | 0.0073314 | 1395.6837 | 12010.3778 | 18015.5667 | 15043.1727
78 | 3808.6639 | 5712.9958 | 0.032695 | 3492.8126 | 5239.2189 | 315.8513 | 0.032526 | 336.303 | 3820.0595 | 5730.0893 | 5389.9087 |  |  |  |  | 78 | 0.0036465 | 7567.7606 | 11351.6409 | 9478.731 | 0.0072522 | 10672.4829 | 16008.7244 | 14052.6956 |  |  |  |  | 0.0036465 | 1418.4392 | 8986.2005 | 13479.3008 | 11255.3467 | 0.0072522 | 1418.4392 | 12090.9228 | 18136.3842 | 15144.0565
79 | 3833.251 | 5749.8765 | 0.032346 | 3511.6236 | 5267.4355 | 321.6274 | 0.032178 | 341.18 | 3843.6988 | 5765.5482 | 5423.2625 |  |  |  |  | 79 | 0.0036075 | 7608.5179 | 11412.7769 | 9529.7801 | 0.0071747 | 10729.9611 | 16094.9417 | 14128.3784 |  |  |  |  | 0.0036075 | 1441.2513 | 9049.7699 | 13574.6549 | 11334.9683 | 0.0071747 | 1441.2513 | 12171.2132 | 18256.8197 | 15244.6213
80 | 3857.9298 | 5786.8947 | 0.032004 | 3530.3345 | 5295.5017 | 327.5953 | 0.031838 | 346.057 | 3867.2381 | 5800.8572 | 5456.4753 |  |  |  |  | 80 | 0.0035694 | 7649.058 | 11473.5871 | 9580.5572 | 0.0070988 | 10787.1331 | 16180.6997 | 14203.6581 |  |  |  |  | 0.0035694 | 1464.12 | 9113.1788 | 13669.7681 | 11414.3888 | 0.0070988 | 1464.12 | 12251.2538 | 18376.8808 | 15344.8734
81 | 3882.7104 | 5824.0656 | 0.031669 | 3548.9467 | 5323.42 | 333.7637 | 0.031505 | 350.934 | 3890.679 | 5836.0186 | 5489.5492 |  |  |  |  | 81 | 0.003532 | 7689.3844 | 11534.0767 | 9631.0666 | 0.0070246 | 10844.0037 | 16266.0055 | 14278.5408 |  |  |  |  | 0.003532 | 1487.0453 | 9176.4305 | 13764.6457 | 11493.6124 | 0.0070246 | 1487.0453 | 12331.0497 | 18496.5746 | 15444.8189
82 | 3907.6029 | 5861.4043 | 0.031341 | 3567.4617 | 5351.1926 | 340.1411 | 0.031179 | 355.811 | 3914.0231 | 5871.0347 | 5522.4865 |  |  |  |  | 82 | 0.0034955 | 7729.5004 | 11594.2507 | 9681.3125 | 0.0069518 | 10900.5775 | 16350.8663 | 14353.0328 |  |  |  |  | 0.0034955 | 1510.0272 | 9239.5284 | 13859.2926 | 11572.6435 | 0.0069518 | 1510.0272 | 12410.6055 | 18615.9082 | 15544.4636
83 | 3932.6172 | 5898.9259 | 0.03102 | 3585.8812 | 5378.8218 | 346.736 | 0.030859 | 360.688 | 3937.2718 | 5905.9078 | 5555.2893 |  |  |  |  | 83 | 0.0034596 | 7769.4093 | 11654.114 | 9731.299 | 0.0068806 | 10956.8593 | 16435.2889 | 14427.1403 |  |  |  |  | 0.0034596 | 1533.0657 | 9302.4758 | 13953.7136 | 11651.486 | 0.0068806 | 1533.0657 | 12489.9257 | 18734.8886 | 15643.8134
84 | 3957.7637 | 5936.6455 | 0.030705 | 3604.2066 | 5406.3099 | 353.5571 | 0.030546 | 365.565 | 3960.4267 | 5940.64 | 5587.9596 |  |  |  |  | 84 | 0.0034245 | 7809.1142 | 11713.6714 | 9781.03 | 0.0068108 | 11012.8534 | 16519.2801 | 14500.869 |  |  |  |  | 0.0034245 | 1556.1608 | 9365.2758 | 14047.9137 | 11730.144 | 0.0068108 | 1556.1608 | 12569.015 | 18853.5224 | 15742.8738
85 | 3983.0522 | 5974.5782 | 0.030397 | 3622.4392 | 5433.6588 | 360.6129 | 0.03024 | 370.442 | 3983.4891 | 5975.2336 | 5620.4994 |  |  |  |  | 85 | 0.0033902 | 7848.6183 | 11772.9275 | 9830.5094 | 0.0067424 | 11068.5643 | 16602.8464 | 14574.2247 |  |  |  |  | 0.0033902 | 1579.3125 | 9427.9316 | 14141.8973 | 11808.6212 | 0.0067424 | 1579.3125 | 12647.8775 | 18971.8163 | 15841.6503
86 | 4008.4928 | 6012.7393 | 0.030095 | 3640.5806 | 5460.8708 | 367.9123 | 0.029939 | 375.319 | 4006.4604 | 6009.6905 | 5652.9108 |  |  |  |  | 86 | 0.0033565 | 7887.9245 | 11831.8868 | 9879.741 | 0.0066754 | 11123.9961 | 16685.9942 | 14647.2131 |  |  |  |  | 0.0033565 | 1602.5208 | 9490.4461 | 14235.6691 | 11886.9216 | 0.0066754 | 1602.5208 | 12726.5177 | 19089.7765 | 15940.1483
87 | 4034.0958 | 6051.1436 | 0.029799 | 3658.6319 | 5487.9479 | 375.4638 | 0.029644 | 380.196 | 4029.3419 | 6044.0129 | 5685.1955 |  |  |  |  | 87 | 0.0033234 | 7927.0359 | 11890.5538 | 9928.7285 | 0.0066097 | 11179.1531 | 16768.7297 | 14719.8395 |  |  |  |  | 0.0033234 | 1625.7857 | 9552.8223 | 14329.2335 | 11965.0487 | 0.0066097 | 1625.7857 | 12804.9396 | 19207.4094 | 16038.3729
88 | 4059.871 | 6089.8065 | 0.029508 | 3676.5947 | 5514.892 | 383.2763 | 0.029355 | 385.073 | 4052.1351 | 6078.2027 | 5717.3555 |  |  |  |  | 88 | 0.003291 | 7965.9552 | 11948.9328 | 9977.4755 | 0.0065453 | 11234.0393 | 16851.059 | 14792.1094 |  |  |  |  | 0.003291 | 1649.1072 | 9615.0631 | 14422.5947 | 12043.0062 | 0.0065453 | 1649.1072 | 12883.1473 | 19324.7209 | 16136.3291
89 | 4085.8287 | 6128.743 | 0.029223 | 3694.4701 | 5541.7052 | 391.3586 | 0.029072 | 389.95 | 4074.8412 | 6112.2618 | 5749.3926 |  |  |  |  | 89 | 0.0032593 | 8004.6853 | 12007.0279 | 10025.9855 | 0.0064821 | 11288.6587 | 16932.988 | 14864.0279 |  |  |  |  | 0.0032593 | 1672.4853 | 9677.1713 | 14515.757 | 12120.7976 | 0.0064821 | 1672.4853 | 12961.1447 | 19441.7171 | 16234.0221
90 | 4111.9788 | 6167.9682 | 0.028944 | 3712.2595 | 5568.3892 | 399.7194 | 0.028794 | 394.827 | 4097.4614 | 6146.1921 | 5781.3086 |  |  |  |  | 90 | 0.0032281 | 8043.2288 | 12064.8433 | 10074.2619 | 0.0064201 | 11343.015 | 17014.5225 | 14935.6001 |  |  |  |  | 0.0032281 | 1695.92 | 9739.1496 | 14608.7244 | 12198.4263 | 0.0064201 | 1695.92 | 13038.9358 | 19558.4037 | 16331.4565
91 | 4138.3315 | 6207.4973 | 0.02867 | 3729.964 | 5594.9459 | 408.3676 | 0.028521 | 399.704 | 4119.997 | 6179.9955 | 5813.1052 |  |  |  |  | 91 | 0.0031975 | 8081.5886 | 12122.3829 | 10122.3081 | 0.0063593 | 11397.1121 | 17095.6682 | 15006.831 |  |  |  |  | 0.0031975 | 1719.4113 | 9801.0007 | 14701.501 | 12275.8957 | 0.0063593 | 1719.4113 | 13116.5242 | 19674.7863 | 16428.6371
92 | 4164.8969 | 6247.3453 | 0.028401 | 3747.5848 | 5621.3772 | 417.3121 | 0.028254 | 404.581 | 4142.4492 | 6213.6738 | 5844.7841 |  |  |  |  | 92 | 0.0031675 | 8119.7671 | 12179.6507 | 10170.1272 | 0.0062996 | 11450.9536 | 17176.4305 | 15077.7253 |  |  |  |  | 0.0031675 | 1742.9592 | 9862.7271 | 14794.0906 | 12353.209 | 0.0062996 | 1742.9592 | 13193.9136 | 19790.8704 | 16525.5685
93 | 4191.685 | 6287.5274 | 0.028137 | 3765.1232 | 5647.6848 | 426.5617 | 0.027991 | 409.458 | 4164.8191 | 6247.2287 | 5876.3469 |  |  |  |  | 93 | 0.0031381 | 8157.767 | 12236.6505 | 10217.7226 | 0.0062411 | 11504.5432 | 17256.8148 | 15148.2879 |  |  |  |  | 0.0031381 | 1766.5637 | 9924.3315 | 14886.4972 | 12430.3693 | 0.0062411 | 1766.5637 | 13271.1077 | 19906.6615 | 16622.2551
94 | 4218.7058 | 6328.0587 | 0.027878 | 3782.5803 | 5673.8705 | 436.1255 | 0.027733 | 414.335 | 4187.1079 | 6280.6619 | 5907.7953 |  |  |  |  | 94 | 0.0031092 | 8195.5907 | 12293.386 | 10265.0973 | 0.0061836 | 11557.8843 | 17336.8264 | 15218.5233 |  |  |  |  | 0.0031092 | 1790.2248 | 9985.8163 | 14978.7244 | 12507.3799 | 0.0061836 | 1790.2248 | 13348.1099 | 20022.1648 | 16718.7015
95 | 4245.9696 | 6368.9544 | 0.027623 | 3799.9572 | 5699.9358 | 446.0124 | 0.02748 | 419.212 | 4209.3168 | 6313.9751 | 5939.1308 |  |  |  |  | 95 | 0.0030808 | 8233.2406 | 12349.8609 | 10312.2544 | 0.0061272 | 11610.9803 | 17416.4705 | 15288.436 |  |  |  |  | 0.0030808 | 1813.9425 | 10047.1839 | 15070.7758 | 12584.2437 | 0.0061272 | 1813.9425 | 13424.9236 | 20137.3854 | 16814.9118
96 | 4273.4863 | 6410.2294 | 0.027374 | 3817.255 | 5725.8825 | 456.2313 | 0.027232 | 424.089 | 4231.4467 | 6347.17 | 5970.355 |  |  |  |  | 96 | 0.003053 | 8270.7191 | 12406.0787 | 10359.1968 | 0.0060718 | 11663.8347 | 17495.752 | 15358.0305 |  |  |  |  | 0.003053 | 1837.7168 | 10108.4367 | 15162.6551 | 12660.9638 | 0.0060718 | 1837.7168 | 13501.5522 | 20252.3284 | 16910.8903
97 | 4301.266 | 6451.899 | 0.027128 | 3834.4747 | 5751.7121 | 466.7913 | 0.026988 | 428.966 | 4253.4988 | 6380.2482 | 6001.4694 |  |  |  |  | 97 | 0.0030256 | 8308.0286 | 12462.0429 | 10405.9275 | 0.0060174 | 11716.4506 | 17574.6758 | 15427.311 |  |  |  |  | 0.0030256 | 1861.5477 | 10169.5771 | 15254.3656 | 12737.543 | 0.0060174 | 1861.5477 | 13577.999 | 20366.9986 | 17006.641
98 | 4329.3188 | 6493.9782 | 0.026887 | 3851.6175 | 5777.4262 | 477.7013 | 0.026748 | 433.843 | 4275.4741 | 6413.2112 | 6032.4754 |  |  |  |  | 98 | 0.0029987 | 8345.1712 | 12517.7569 | 10452.4492 | 0.0059639 | 11768.8312 | 17653.2469 | 15496.2818 |  |  |  |  | 0.0029987 | 1885.4352 | 10230.6072 | 15345.9108 | 12813.9842 | 0.0059639 | 1885.4352 | 13654.2672 | 20481.4008 | 17102.168
99 | 4357.6548 | 6536.4823 | 0.026651 | 3868.6843 | 5803.0264 | 488.9705 | 0.026513 | 438.72 | 4297.3737 | 6446.0605 | 6063.3746 |  |  |  |  | 99 | 0.0029723 | 8382.1493 | 12573.224 | 10498.7648 | 0.0059114 | 11820.9798 | 17731.4697 | 15564.947 |  |  |  |  | 0.0029723 | 1909.3793 | 10291.5294 | 15437.2941 | 12890.2901 | 0.0059114 | 1909.3793 | 13730.3599 | 20595.5398 | 17197.4752
100 | 4386.2841 | 6579.4262 | 0.026418 | 3885.6761 | 5828.5142 | 500.608 | 0.026281 | 443.597 | 4319.1985 | 6478.7977 | 6094.1682 |  |  |  |  | 100 | 0.0029464 | 8418.965 | 12628.4475 | 10544.8769 | 0.0058598 | 11872.8993 | 17809.349 | 15633.3106 |  |  |  |  | 0.0029464 | 1933.38 | 10352.3458 | 15528.5187 | 12966.4635 | 0.0058598 | 1933.38 | 13806.2801 | 20709.4202 | 17292.5664
[16 empty] | 101 | 0.0029209 | 8455.6203 | 12683.4305 | 10590.7883 | 0.0058091 | 11924.5928 | 17886.8892 | 15701.3765 |  |  |  |  | 0.0029209 | 1957.4373 | 10413.0584 | 15619.5877 | 13042.507 | 0.0058091 | 1957.4373 | 13882.0309 | 20823.0463 | 17387.4453
[16 empty] | 102 | 0.0028958 | 8492.1175 | 12738.1762 | 10636.5015 | 0.0057593 | 11976.0631 | 17964.0947 | 15769.1486 |  |  |  |  | 0.0028958 | 1981.5512 | 10473.6695 | 15710.5042 | 13118.4232 | 0.0057593 | 1981.5512 | 13957.6151 | 20936.4227 | 17482.1157
[16 empty] | 103 | 0.0028712 | 8528.4585 | 12792.6877 | 10682.0191 | 0.0057103 | 12027.3132 | 18040.9698 | 15836.6308 |  |  |  |  | 0.0028712 | 2005.7217 | 10534.181 | 15801.2714 | 13194.2147 | 0.0057103 | 2005.7217 | 14033.0357 | 21049.5536 | 17576.5811
[16 empty] | 104 | 0.002847 | 8564.6452 | 12846.9678 | 10727.3436 | 0.0056622 | 12078.3458 | 18117.5187 | 15903.8265 |  |  |  |  | 0.002847 | 2029.9488 | 10594.5948 | 15891.8922 | 13269.8839 | 0.0056622 | 2029.9488 | 14108.2954 | 21162.4431 | 17670.845
[16 empty] | 105 | 0.0028232 | 8600.6797 | 12901.0196 | 10772.4773 | 0.0056148 | 12129.1637 | 18193.7456 | 15970.7396 |  |  |  |  | 0.0028232 | 2054.2325 | 10654.913 | 15982.3696 | 13345.4334 | 0.0056148 | 2054.2325 | 14183.397 | 21275.0956 | 17764.9108
[16 empty] | 106 | 0.0027998 | 8636.5639 | 12954.8459 | 10817.4228 | 0.0055683 | 12179.7696 | 18269.6544 | 16037.3735 |  |  |  |  | 0.0027998 | 2078.5728 | 10715.1375 | 16072.7063 | 13420.8654 | 0.0055683 | 2078.5728 | 14258.3432 | 21387.5148 | 17858.782
[16 empty] | 107 | 0.0027768 | 8672.2996 | 13008.4494 | 10862.1822 | 0.0055225 | 12230.1661 | 18345.2491 | 16103.7317 |  |  |  |  | 0.0027768 | 2102.9697 | 10775.2701 | 16162.9052 | 13496.1823 | 0.0055225 | 2102.9697 | 14333.1366 | 21499.7049 | 17952.4618
[16 empty] | 108 | 0.0027541 | 8707.8886 | 13061.8329 | 10906.758 | 0.0054774 | 12280.3558 | 18420.5336 | 16169.8175 |  |  |  |  | 0.0027541 | 2127.4232 | 10835.3126 | 16252.969 | 13571.3865 | 0.0054774 | 2127.4232 | 14407.7798 | 21611.6697 | 18045.9535
[16 empty] | 109 | 0.0027318 | 8743.3328 | 13114.9992 | 10951.1524 | 0.0054331 | 12330.3411 | 18495.5117 | 16235.6344 |  |  |  |  | 0.0027318 | 2151.9333 | 10895.2669 | 16342.9004 | 13646.4801 | 0.0054331 | 2151.9333 | 14482.2752 | 21723.4129 | 18139.2601
[16 empty] | 110 | 0.0027099 | 8778.6339 | 13167.9508 | 10995.3675 | 0.0053895 | 12380.1247 | 18570.187 | 16301.1855 |  |  |  |  | 0.0027099 | 2176.5 | 10955.1347 | 16432.702 | 13721.4653 | 0.0053895 | 2176.5 | 14556.6255 | 21834.9383 | 18232.3849
[16 empty] | 111 | 0.0026883 | 8813.7936 | 13220.6903 | 11039.4055 | 0.0053466 | 12429.7088 | 18644.5633 | 16366.474 |  |  |  |  | 0.0026883 | 2201.1233 | 11014.9177 | 16522.3765 | 13796.3444 | 0.0053466 | 2201.1233 | 14630.833 | 21946.2495 | 18325.3308
[16 empty] | 112 | 0.0026671 | 8848.8135 | 13273.2203 | 11083.2685 | 0.0053044 | 12479.096 | 18718.644 | 16431.5032 |  |  |  |  | 0.0026671 | 2225.8032 | 11074.6176 | 16611.9263 | 13871.1194 | 0.0053044 | 2225.8032 | 14704.9 | 22057.35 | 18418.1009
[16 empty] | 113 | 0.0026462 | 8883.6955 | 13325.5432 | 11126.9587 | 0.0052628 | 12528.2885 | 18792.4327 | 16496.276 |  |  |  |  | 0.0026462 | 2250.5397 | 11134.236 | 16701.354 | 13945.7923 | 0.0052628 | 2250.5397 | 14778.829 | 22168.2435 | 18510.698
[16 empty] | 114 | 0.0026256 | 8918.441 | 13377.6614 | 11170.4779 | 0.0052219 | 12577.2885 | 18865.9328 | 16560.7955 |  |  |  |  | 0.0026256 | 2275.3328 | 11193.7746 | 16790.6619 | 14020.3653 | 0.0052219 | 2275.3328 | 14852.6222 | 22278.9332 | 18603.125
[16 empty] | 115 | 0.0026053 | 8953.0516 | 13429.5774 | 11213.8283 | 0.0051816 | 12626.0984 | 18939.1476 | 16625.0646 |  |  |  |  | 0.0026053 | 2300.1825 | 11253.235 | 16879.8524 | 14094.8403 | 0.0051816 | 2300.1825 | 14926.2818 | 22389.4227 | 18695.3847
[16 empty] | 116 | 0.0025854 | 8987.529 | 13481.2935 | 11257.0117 | 0.0051419 | 12674.7204 | 19012.0806 | 16689.0862 |  |  |  |  | 0.0025854 | 2325.0888 | 11312.6186 | 16968.928 | 14169.2192 | 0.0051419 | 2325.0888 | 14999.81 | 22499.715 | 18787.4799
[16 empty] | 117 | 0.0025657 | 9021.8746 | 13532.8119 | 11300.0301 | 0.0051028 | 12723.1565 | 19084.7347 | 16752.8631 |  |  |  |  | 0.0025657 | 2350.0517 | 11371.9272 | 17057.8907 | 14243.504 | 0.0051028 | 2350.0517 | 15073.209 | 22609.8136 | 18879.4133
[16 empty] | 118 | 0.0025464 | 9056.09 | 13584.135 | 11342.8853 | 0.0050643 | 12771.4089 | 19157.1134 | 16816.3981 |  |  |  |  | 0.0025464 | 2375.0712 | 11431.162 | 17146.743 | 14317.6965 | 0.0050643 | 2375.0712 | 15146.481 | 22719.7215 | 18971.1875
[16 empty] | 119 | 0.0025273 | 9090.1766 | 13635.2648 | 11385.5792 | 0.0050264 | 12819.4797 | 19229.2196 | 16879.6941 |  |  |  |  | 0.0025273 | 2400.1473 | 11490.3247 | 17235.4871 | 14391.7986 | 0.0050264 | 2400.1473 | 15219.6279 | 22829.4419 | 19062.805
[16 empty] | 120 | 0.0025086 | 9124.1358 | 13686.2037 | 11428.1137 | 0.0049891 | 12867.371 | 19301.0565 | 16942.7535 |  |  |  |  | 0.0025086 | 2425.28 | 11549.4166 | 17324.125 | 14465.8121 | 0.0049891 | 2425.28 | 15292.6518 | 22938.9778 | 19154.2686
[16 empty] | 121 | 0.0024901 | 9157.9691 | 13736.9536 | 11470.4904 | 0.0049523 | 12915.0846 | 19372.6269 | 17005.5791 |  |  |  |  | 0.0024901 | 2450.4693 | 11608.4393 | 17412.6589 | 14539.7388 | 0.0049523 | 2450.4693 | 15365.5548 | 23048.3322 | 19245.5806
[16 empty] | 122 | 0.0024718 | 9191.6779 | 13787.5168 | 11512.7111 | 0.004916 | 12962.6226 | 19443.934 | 17068.1735 |  |  |  |  | 0.0024718 | 2475.7152 | 11667.3939 | 17501.0909 | 14613.5804 | 0.004916 | 2475.7152 | 15438.3387 | 23157.5081 | 19336.7435
[16 empty] | 123 | 0.0024539 | 9225.2635 | 13837.8952 | 11554.7776 | 0.0048803 | 13009.987 | 19514.9804 | 17130.5391 |  |  |  |  | 0.0024539 | 2501.0177 | 11726.282 | 17589.4231 | 14687.3386 | 0.0048803 | 2501.0177 | 15511.0055 | 23266.5083 | 19427.7597
[16 empty] | 124 | 0.0024362 | 9258.7273 | 13888.0909 | 11596.6915 | 0.0048451 | 13057.1795 | 19585.7692 | 17192.6785 |  |  |  |  | 0.0024362 | 2526.3768 | 11785.1049 | 17677.6574 | 14761.0151 | 0.0048451 | 2526.3768 | 15583.5571 | 23375.3357 | 19518.6317
[16 empty] | 125 | 0.0024187 | 9292.0705 | 13938.1058 | 11638.4544 | 0.0048104 | 13104.202 | 19656.303 | 17254.5942 |  |  |  |  | 0.0024187 | 2551.7925 | 11843.8639 | 17765.7958 | 14834.6116 | 0.0048104 | 2551.7925 | 15655.9954 | 23483.9931 | 19609.3616
Note on B2: Bill DeKeyser: Rev 5E of the calculator was used to pull the formulas for the 1800 and generate the curve.
Note on D2: Bill DeKeyser: Same information used to generate curves on Data and Formula tab
Note on N2: Bill DeKeyser: Tested with Molded D Plunger (Known to be high trip point) and has addition shift due to 4 cavity body
Note on J4: Bill DeKeyser: Hard coded from trendline chart
Note on AO4: Bill DeKeyser: Hard coded from trendline chart
Note on AT4: Bill DeKeyser: Hard Coded from Trendline chart
Note on J5: Bill DeKeyser: Hard coded from trendline chart
Note on AO5: Bill DeKeyser: Hard coded from trendline chart
Note on AT5: Bill DeKeyser: Hard coded from trendline chart
Note on J6: Bill DeKeyser: Pressure Drop was readjusted to insure that 1800 at 10 psi was maintained
Note on AO6: Bill DeKeyser: Hard coded from trendline chart
Note on AT6: Bill DeKeyser: Hard coded from trendline chart
Note on AO7: Bill DeKeyser: This value needs to be shifted using goal seek to align 3900 at 10 psi. This value needs to be copied and pasted to the Data and Formulas Tab
Note on AT7: Bill DeKeyser: This value needs to be shifted using goal seek to align 5500 at 10 psi. This value needs to be copied and pasted into the Data and Formulas tab.
Note on J8: Bill DeKeyser: Used to generate the theoretical curve based on the data, by setting the flow at 10 psi and offsetting the Min trip flow curve
Note on L10: Bill DeKeyser: This is the theortical curve for the test data, used to compare shift to test data
Note on AH10: Bill DeKeyser: Data is average of 25 samples tripped 5 times each at each pressure
Note on AQ10: Bill DeKeyser: This is the theortical curve for the test data, used to compare shift to test data
Note on AV10: Bill DeKeyser: This is the theortical curve for the test data, used to compare shift to test data
Note on G11: Bill DeKeyser: The difference between the min trip flow from the Cv generated data and the old curve fit data. Graphed to establish the shift line
Note on I11: Bill DeKeyser: The amount added to the minimum flow due to the shift generated shift equation.
Note on AB11: Bill DeKeyser: This is the theortical curve for the test data, used to compare shift to test data
Note on AF11: Bill DeKeyser: This is the theortical curve for the test data, used to compare shift to test data
Note on AN11: Bill DeKeyser: The amount added to the minimum flow due to the shift generated shift equation.
Note on AS11: Bill DeKeyser: The amount added to the minimum flow due to the shift generated shift equation.