EQUIPMENT SPECIFICATION

GAI-TRONICS ADDRESSABLE AMPLIFIED SPEAKER

(AND PUBLIC ADDRESS HEAD-END PRODUCTS)

EQUIPMENT SPECIFICATION

GAI-TRONICS’ ADDRESSABLE AMPLIIFED SPEAKER

(AND PUBLIC ADDRESS HEAD-END PRODUCTS)

INDEX

Part 1													Page

1.0.0    Scope and Intent	4

2.0.0    Seller Warranties	4

3.0.0    Workmanship	4

4.0.0    Material and Construction	4

5.0.0    Installation: Equipment and wiring to be installed by Purchaser	4

6.0.0    Operation and Maintenance Instructions	4

7.0.0    Environmental Conditions	5

8.0.0    Equipment Operation	5

9.0.0    Field Wiring	....5

10.0.0  Equipment	5-16

10.1.0   Addressable Amplified Speaker, 600-Ohm, 0dBm Input	5-8

10.1.1  Description……………………………………………………..………………	5,6

10.1.2  Interconnection……………………………………………………..………………	6

10.1.3  Features……………………………………………………..………………	6

10.1.4  Performance Specification………………………………………………..………………	7

10.1.5  Peripheral Equipment and Accessories………………………..………………	7,8

10.1.6  Equipment Manufacturer and Model Numbers…………………………..………………	8

10.2.0	  Addressable Amplified RF Speakers, VHF/UHF Operation	8-12

10.2.1  Description……………………………………………………..………………	8,9

10.2.2  Interconnection……………………………………………………..………………	9

10.2.3  Features……………………………………………………..………………	9,10

10.2.4  Performance Specification………………………………………………..……………	10,11

10.2.5  Peripheral Equipment and Accessories………………………..………………	11,12

10.2.6  Equipment Manufacturer and Model Numbers…………………………..………………	12

10.3.0	  Audio Control Center Deskset	12-14

10.2.1  Description……………………………………………………..………………	12

10.2.2  Interconnection……………………………………………………..………………	13

10.2.3  Features……………………………………………………..………………	13

10.2.4  Performance Specification………………………………………………..……………	13

10.2.5  Peripheral Equipment and Accessories………………………..………………	13

10.2.6  Equipment Manufacturer and Model Numbers…………………………..………………	14

10.4.0	  Audio Messenger Interface	14-16

10.2.1  Description……………………………………………………..………………	14

10.2.2  Interconnection……………………………………………………..………………	14

10.2.3  Features……………………………………………………..………………	14-15

10.2.4  Performance Specification………………………………………………..……………	15

10.2.5  Peripheral Equipment and Accessories………………………..………………	15

10.2.6  Equipment Manufacturer and Model Numbers…………………………..………………	16

10.2.0	  AMI to Deskset Interface	16

10.2.1  Description……………………………………………………..………………	16

10.2.2  Interconnection……………………………………………………..………………	16

10.2.5  Peripheral Equipment and Accessories………………………..………………	16

10.2.6  Equipment Manufacturer and Model Numbers…………………………..………………	16

Part 2

11.0.0  Quantity Specification…..	17,18

11.1.0    Addressable Amplified Speakers…………………………………..………………	17

___ 13353 600 Ohm, 0 dBm Input Operation…………………………………..……………..…	17

___ 13363 VHF (154-174MHz) Operation……………………………………..………………	17

___ 13373 UHF (450-470MHz) Operation…………………………………..………………	17

11.2.0	Access Control Center Deskset

___ ACC2500 Access Control Center Deskset…………………………………..……………..…	17

11.3.0	Access Control Center Deskset

___ ACC2500 Access Control Center Deskset…………………………………..……………..…	17

11.4.0	Access Control Center Deskset

___ ACC2500 Access Control Center Deskset…………………………………..……………..…	17

11.5.0   Peripheral Equipment and Accessories………………………………..……………….17,18

___  BB133 AAS Battery Back-up Kit………………………………..……………..…	17

___  XB001Long-Life Battery Enclosure ………………………………..……………..…	17

___  40201-008 Long-Life Battery, 18Ah ………………………………..……………..…	17

___  GTRFP7784-108 Solar Panel Array………………………………..……………..…	17

___  SPK200 Solar Panel Interface Kit………………………………..……………..…	17

___  190-002PS Weatherproof Power Supply Kit………………………………..……………..…	17

___  XAC1000A CARD Suite Programming Software………………………..……………..…	17

___  XAC0004A AAS Programming Cable………………………………..……………..…	17

___  19101-024 RF Module Programming Kit………………………………..……………..…	18

___  GTRFP6432-106 Free-standing Tripod for AAS…………………………..……………..…	18

___  TPD001 Tripod Mounting Kit for for AAS………………………………..……………..…	18

___  231-001 Pole Mounting Kit for for AAS………………………………..……………..…	18

___  230-001 Pole Mounting Kit for XB001………………………………..……………..…	18

___  40408-009 Battery Charger for BB133 Battery Back-up Kit…………………………..…	18

___  40408-011 Battery Charger for 40201-008 18Ah Battery……...……..……..……………….18

___  12506-001 Remote Volume Control L-Pad………...………………………..……………….18

#### PART 1

  - Scope and Intent

This specification identifies and details the equipment, accessories, and peripherals necessary to broadcast live voice, pre-recorded voice messages, and/or alarm tones via distributed speakers for hard-wired installation applications and applications where wiring/cabling is not feasible.  It covers the furnishing of all labor, materials, and services in connection with the design, fabrication, and delivery of the equipment specified herein. This specification will identify Addressable Amplified Speaker (AAS), Audio Messenger Interface (AMI), and Audio Control Center (ACC) features and functionality as well as peripheral products.

All supporting documentation mentioned in this specification (literature and manuals) can be found on the GAI-Tronics Website: www.gai-tronics.com.

2.0.0     Seller Warranties

  - The Seller warrants the satisfactory and successful operation of all equipment furnished under this specification at the ratings, under the conditions, and for the type of service specified herein.

  - Goods manufactured by the seller are warranted to be free from defects in material and workmanship until one year after the date of shipment.  Equipment supplied by but not manufactured by the seller shall be subject to the original equipment manufacturer’s standard warranty.

  - Workmanship

All work shall be performed in accordance with the best modern practice in design, manufacture, and fabrication of all material and apparatus by this specification, notwithstanding any omission from the specifications or drawings.

4.0.0     Material and Construction

All materials used in the construction of the apparatus shall be new and selected as the best available for the intended purpose, considering long life and best engineering practices.  Factors of safety shall be used throughout the design.  Only heavy-duty industrial components rated to operate within the temperature ranges and other environmental conditions specified in Paragraph 7 shall be used.

  - Installation:  Equipment and wiring to be installed by the Purchaser.

Seller shall provide technical guidance during installation and/or testing, via telephone, at no additional charge.  After installation is completed, the Seller shall be prepared to perform a checkout of the system.  If required by the buyer, a factory technician shall visit the job site to assist with system layout and design (pre-sale) or to make all necessary adjustments and instruct the operating and maintenance personnel on the proper use and care of the system (post-sale).  Charges for the service are to be on a per diem basis (including travel time), plus all expenses on a cost plus basis.

  - Operation and Maintenance Instructions

All equipment requiring continued interaction, service, or support shall be provided with complete operation (user) and maintenance (service) manuals.  All available documentation shall be packaged with the equipment and readily accessible via the manufacturer’s website.

  - Environmental Conditions

Equipment shall be suitable for use in designated environmental conditions per the appropriately listed performance specification.

  - Equipment Operation

Specified equipment shall provide one-way public address broadcast (P.A.) capability from a UHF or VHF radio system or from a hard-wired, 600 Ohm audio input.  The P.A. system shall be of a distributed design to eliminate the possibility of a single component failure disabling the entire system or system segments (zones or groups).  Additionally, the system shall be capable of allowing selective individual speaker broadcasts, speaker group broadcasts, or all speaker broadcasts.  This selective broadcast capability shall controlled via DTMF signal or 2-Tone signal addresses.

Each AAS shall be self-contained, providing local amplification of the received audio signal.  Output volume shall be adjustable between 83dB and 116dB SPL (measured at 1-meter on axis), via PC-programming, external volume control, or remote DTMF volume control.  Each AAS shall also be capable of being programmed to perform automatic volume adjustment based on ambient noise level.

Each AAS shall be capable of being PC-programmed for non-selective (all-call), DTMF selective, or 2-Tone selective.  If in a “selective” mode of operation, each AAS shall be capable of accepting up to eight (8) specific DTMF or 2-Tone addresses (RF version only).

  - Field Wiring

All local power wiring shall conform to the specific equipment’s installation instructions and local and national codes.

External antenna wiring (if applicable) shall be routed through a different enclosure entrance than any external power wiring, in compliance with the manufacturer’s installation instructions.

10.0.0   Equipment

10.1.0	Addressable Amplified Speaker, 600-Ohm, 0dBm Input

    - Description

This Addressable Amplified Speaker (AAS) shall be designed for use in a hard-wired paging system, accepting any 600 Ohm, 0 dBM audio input.  The AAS shall be capable of operating in two distinct modes.  In one mode, the speaker shall broadcast any 600 Ohm, 0 dBM audio signal provided to it via a twisted wire pair.  This mode shall also require a dedicated contact closure input (twisted wire pair) to provide circuit activation.  A second mode of operation shall allow access to the AAS via a DTMF address of 2-8 digits.  This mode of operation shall require only a single, twisted wire audio pair.  Each AAS shall be capable of a accepting up to 8 different DTMF addresses for activation.  The operation mode selection shall be PC-programmable.

The AAS shall contain audio circuitry for amplification of the received audio signal.  This circuitry shall provide a minimum 8-Watt output, producing a maximum volume of 116dB SPL measured at 1-meter on axis.  Maximum current draw at full power output with a nominal 13.8 V dc input shall be 1.0 Ampere.  The AAS shall require a 12 V dc power input (13.8 Vdc when used with a back-up battery) and shall be factory-shipped with a 120 V ac - 15 V dc plug-in power supply.  The AAS shall be suitable for internal or external battery-only or battery back-up operation.  The AAS shall also be suitable for direct or solar external power operation.  A back-up battery shall be capable of being mounted directly inside the AAS assembly.  It shall carry a minimum rating of 2.8Ah and shall be rechargeable via the AAS circuitry or external battery charger, providing a minimum 2-hour output at full power when direct power is lost.  An external battery shall be available for long-term, temporary operation.  The external battery configuration shall carry a minimum rating of 18Ah and shall be rechargeable via the AAS circuitry or external battery charger, providing a minimum 13-hour output at full power.  The AAS shall be capable of providing a low battery alert signal when the battery drops below and acceptable voltage level.  A solar power option shall also be available for trickle-charging the 18Ah, long-term, battery.  In addition to the provided plug-in power supply, a minimum 1.7 Ampere weatherproof power supply shall be available for providing power to the Addressable Amplified Speakers.  This power supply shall be capable of direct mounting to the exterior of the AAS and shall accept an input of 120-240Vac to provide an adjustable 15 Vdc output.

Each AAS shall be capable of being PC-programmed for a specific volume level, remote volume control, or automatic volume control.  In automatic volume control mode, the AAS shall sample the surrounding ambient noise and automatically adjust its own speaker level output to a pre-programmed level above ambient noise.

Each AAS shall be capable of providing a dry contact closure output when the unit is active.  This output shall be programmable and available when the AAS is used in any mode of operation.  When in DTMF selective mode of operation, the output shall be programmable (on, off, timed) in correlation with each programmed address.

    - Interconnection

Interconnecting wiring shall be limited to audio and activation telephone wires (2-pair, if control pair is required), external 15 V dc power, and/or external coaxial cable for antenna connection.  All external cabling shall be entered through the enclosure per the manufacturer’s installation instructions.  Required external antenna cable shall be connectorized by the installer and connected directly to the RF source located inside the AAS enclosure.  External power supply wiring shall be connected to a screw terminal located inside the AAS enclosure.

Each AAS shall be capable of providing feed-through audio and control to another AAS.  If connected in this feed-through manner, the connected AAS shall be capable of being programmed to either duplicate the operation of the feeder or lead AAS or operating as an individual unit with no involvement of the lead AAS.

    - Features

This Addressable Amplified Speaker shall provide the following standard features and functionality:

- Built-in 8-Watt Amplifier

- Accepts 600-Ohm, 0dBm Audio Input

- Addressable (individual, zoned, all-page) via DTMF, 8 addresses

- Remote DTMF Volume Control, 83-116 dB SPL, in all operating modes

- 15 V dc Input Power

- Battery Back-up Option w/ Low Battery Alert

- Feed-Through Connection

- Automatic Volume Level Control

- Addressable Output Control

- External Long-Life Battery Option

- Solar Panel Power Option

- Surface or Pole Mounting

- Weatherproof

- Power Saver Feature

- PC Programmable

    - Performance Specification

This Addressable Amplified Speaker shall meet the following performance and physical specifications:

Electrical

Output Power: . . . . . . . . . . . . . . . . . . .  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 8 watt continuous

Impedance: . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 8 ohms

Output Range (dB) . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 83-116 dB (@ 1 meter on axis)

Frequency Response: . . . . . . .  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 450 Hz to 3000 Hz +/-5 dB

Dispersion: . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 90 degrees nominal horizontal coverage; +40, -60 vertical coverage

Mechanical

Mounting . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . Direct wall mounting (pole mounting with kit)

Conduit Entry . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . Dual 3/4" NPT female entry

Electrical Connections . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .Terminal block

Housing Material . . . . . . . . . . .  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . Glass-reinforced polyester

Dimensions . . . . . . . . . . . . . . .  . . . . . . . . . . . . . . . . . . . . 9.52 (241.8) x 8.02 (203.7)W x 8.12 (206.2)D; inches (mm)

Net Weight . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 6.6 lbs.

# Environmental

Temperature Range . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . -20º C to +60º C

Weatherproof Rating . . . .. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . Rainproof

Humidity . . . . . . . . . . . . .  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 95% non-condensing

Power Requirements

Voltage (V dc) . . . . . . . . .   . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 12.6 min./13.8 typ./15 max.

Current Draw . . . . . . . . . . . . . . . . . . . . . . . . . . . . . …… . 100 mA/sleep mode to 900 mA max. @ 13.8 V dc input/8W output

    - Peripheral Equipment and Accessories

The following peripheral equipment and accessories shall be offered in support of Addressable Amplified Speaker:

Battery Back-Up Kit shall be offered to provide power back-up in the case of the loss of direct power.   The back-up time duration shall be a minimum of 120 minutes at continuous full output power. The kit shall provide the battery and any necessary mounting hardware for installation inside the AAS.

Long-Life Battery Enclosure shall be offered to house an 18 Ah battery (provided separately).  The enclosure shall also be designed to house the solar charge regulator module found in the solar panel interface kit.  The kit shall include a connection cable that plugs into a weather proof connector located on the enclosure’s side, with the other end terminating inside the AAS enclosure.  Fully-charged, the 18 Ah battery shall provide a minimum of 13 hours of AAS operation at full output (8W).   Calculating the battery life based on 20-second duty-cycles, a fully charged battery shall provide over 3,000 cycles at maximum output.

Solar Panel Array shall be offered to provide trickle-charging of AAS battery operation (long-life battery).  The solar panel array shall provide a minimum 30-Watt output and shall include an integral connection cable that is minimally 15 feet in length.  The solar panel shall interconnect with the long-life battery enclosure.

Solar Panel Interface Kit shall be offered to provide materials necessary to mount the solar panel array to a pole (max. 4-inches in diameter) or flat surface.  The kit shall include all necessary hardware with the exception of mounting bands or U-bolts, which shall be provided by the installer. The kit shall also include a solar panel charge regulator module that shall mount inside the Long-Life Battery Enclosure.

Weatherproof Power Supply Kit shall be offered to provide external power to the RF Call Box.  The power supply shall provide a regulated 15.0 V dc and maximum, 1.7 amperes to the RF Call Box and shall be suitable for mounting via a ¾” NPT pipe nipple and hub to the bottom of the AAS.  The kit shall include all necessary mounting hardware, wire harnesses, power supply, and weatherproof enclosure.  The power supply shall be capable of accepting an input of 120 – 240 V ac.

Programming Software shall be offered to provide programming of the AAS features, including but not limited to volume level, mode selection, and selective addresses.

Pole Mounting Kit shall be offered to mount the AAS to a pole with a maximum 4-inch diameter.

Pole Mounting Kit shall be offered to mount the Long-Life Battery Enclosure to a pole with a maximum 4-inch diameter.

Battery Charger shall be offered for recharging both the 2.8Ah and the 18Ah batteries.

Remote Volume Control shall be offered in the form of an L-pad with the capability of mounting to a single-gang outlet box and hardwiring to the AAS.

    - Equipment Manufacturer and Model Numbers

The Addressable Amplified Speaker shall be GAI-Tronics Model 13353.  AAS peripherals and accessories shall be GAI-Tronics models numbers, specified as:

- BB133 Battery Back-up Kit

- XB001 Long-Life Battery Enclosure

- 40201-008 18 Ah Battery

- GTRFP7784-108 30-Watt Solar Panel Array

- SPK200  Solar Panel Interface Kit

- 190-002PS Weatherproof Power Supply Kit

- XAC1000A  CARD Suite Programming Software

- XAC0004A Programming Cable

- 231-001  Pole Mounting Kit for AAS

- 230-001  Pole Mounting Kit for XB001

- 40408-009 Battery Charger for 2.8 Ah battery

- 40408-011 Battery Charger for 18 Ah battery

- 12506-001 Remote Volume Control L-Pad

  - Addressable Amplified RF Speaker, VHF/UHF Operation

    - Description

These Addressable Amplified Speakers (AAS) shall be designed for use in a radio system utilizing a licensed VHF (154-174MHz) or UHF (450-470MHz) frequency.  The AAS shall be capable of operating in two distinct modes.  In one mode, the speaker shall broadcast audio received on its programmed frequency and PL code (if applicable).  In this mode, the carrier detect provided by the integral radio receiver circuit shall activate the broadcast circuitry.  A second mode of operation shall allow access to the AAS via a DTMF address of 2-8 digits or 2-Tone address.  In this mode, the speaker broadcast circuitry will not activate until the required address is received via the RF airwaves.

Each RF AAS shall also be capable of being controlled by a hard-wired, 600 Ohm audio input, as described in section 10.1.1.  This ability shall exist whether the AAS is operating in an “all-call” mode or in a selective, addressable mode.  The “all-call” operation mode (generic) shall be expected to require a contact closure pair for circuit activation.

These Addressable Amplified Speakers shall contain a receiver module with integral antenna and audio amplifier circuitry for amplification of the received RF audio signal.  This circuitry shall provide a minimum 8-Watt output, producing a maximum volume of 116dB SPL measured at 1-meter on axis.  Maximum current draw at full power output with a nominal 13.8 V dc input shall be 1.0 Ampere.

The AAS shall require a 12 V dc power input and shall be factory-shipped with a 120 V ac - 	12 V dc plug-in power supply.  The AAS shall be suitable for internal or external battery-only or battery back-up operation.  The AAS shall also be suitable for direct or solar external power operation.  A back-up battery shall be capable of being mounted directly inside the AAS assembly.  It shall carry a minimum rating of 2.8Ah and shall be rechargeable via the AAS circuitry or external battery charger, providing a minimum 2-hour output at full power when direct power is lost.  An external battery shall be available for long-term, temporary operation.  The external battery configuration shall carry a minimum rating of 18Ah and shall be rechargeable via the AAS circuitry or external battery charger, providing a minimum 16-hour output at full power.  The AAS shall be capable of providing a low battery alert signal when the battery drops below 11.5 volts.  A solar power option shall also be available for trickle-charging the 18Ah, long-term, battery.  In addition to the provided plug-in power supply, a minimum 1.5 Ampere weatherproof power supply shall be available for providing power to the Addressable Amplified Speakers.  This power supply shall be capable of direct mounting to the exterior of the AAS and shall accept an input of 120-240Vac to provide an adjustable 15 Vdc output.

Each AAS shall be capable of being PC-programmed for frequency, specific volume level, remote volume control, or automatic volume control.  In automatic volume control mode, the AAS shall sample the surrounding ambient noise and automatically adjust its own speaker level output to a pre-programmed level above ambient.

These speakers shall also be capable of operating with an external antenna if required by the RF system layout.

    - Interconnection

Interconnecting wiring shall be limited to external 12 V dc power and/or external coaxial cable for antenna connection.  All external cabling shall be entered through the enclosure per the installation instructions.  Required antenna cable shall be connectorized by the installer and connected directly to the RF source located inside the AAS enclosure.  External power supply wiring shall be connected to a screw terminal located inside the AAS enclosure.

Each AAS shall be capable of providing feed-through audio and control to another AAS.  If connected in this feed-through manner, the connected AAS shall be capable of being programmed to either duplicate the operation of the feeder or lead AAS or operate as an individual unit with no involvement of the lead AAS.

    - Features

These Addressable Amplified Speakers shall provide the following standard features and functionality:

- Built-in 8-Watt Amplifier

- Built-in VHF or UHF Receiver Module with Antenna

- Addressable (individual, zoned, all-page) via DTMF or 2-Tone, 8 addresses

- Remote DTMF Volume Control, 83-116 dB SPL, in all operating modes

- 12 V dc Input Power

- Battery Back-up Option w/ Low Battery Alert

- Feed-Through connection

- Automatic Volume Level Control

- Addressable Output Control

- External Long-Life Battery Option

- Solar Panel Power Option

- Surface or Pole Mounting

- Rainproof Rating

- Power Saver Feature

- PC Programmable

    - Performance Specification

This Addressable Amplified Speaker shall meet the following performance and physical specifications:

Electrical

Output Power: . . . . . . . . . . . . . . . . . . .  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 8 watt continuous

Impedance: . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 8 ohms

Output Range (dB) . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 83-116 dB (@ 1 meter on axis)

Frequency Response: . . . . . . .  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 450 Hz to 3000 Hz +/-5 dB

Dispersion: . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 90 degrees nominal horizontal coverage; +40, -60 vertical coverage

Mechanical

Mounting . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . Direct wall mounting (pole mounting with kit)

Conduit Entry . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . Dual 3/4" NPT female entry

Electrical Connections . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .Terminal block

Housing Material . . . . . . . . . . .  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . Glass-reinforced polyester

Dimensions . . . . . . . . . . . . . . .  . . . . . . . . . . . . . . . . . . . . 9.52 (241.8) x 8.02 (203.7)W x 8.12 (206.2)D; inches (mm)

Net Weight . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 7.3 lbs.

# Environmental

Temperature Range . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . -20º C to +60º C

Weatherproof Rating . . . .. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . Rainproof

Humidity . . . . . . . . . . . . .  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 95% non-condensing

Power Requirements

Voltage (V dc) . . . . . . . . .   . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 12.6 min./13.8 typ./15 max.

Current Draw . . . . . . . . . . . . . . . . . . . . . . . . . . ……. 100 mA/sleep mode to 1.0A max. @ 13.8 V dc input/8W output

RF Modules

General

Frequency Range . . .  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .VHF: 154-174 MHz

UHF: 450-470 MHz

Antenna Impedance . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 50 Ohms

Operating Voltage . . . . . . . . . . . . . . . . .. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 9-18 V dc, 12 V dc nominal

Encoder/Decoder . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . CTCSS/CDCSS

### Receiver (measurement procedures made per ANSI/TIA/EIA-603

Sensitivity (12 dB SINAD), UHF and VHF . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . @ 25KHz spacing 0.28 µV

@ 12.5KHz spacing 0.30µV

Intermodulation . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .>60 dB

Spurious Rejection (100KHz-4GHz) .  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .>60 dB

Approvals

FCC Identifier . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . VHF: AIERT 17-142

UHF: AIERT 17-442

FCC Compliance . . . . . . . . . . . . . . . . . . . . . .. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . Part 90

VHF Antenna (Helical)

Mounting . . . . . . . . . . . . . . . . . . . . . . . . . .  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . BNC

Impedance . . . . . . . . . . . . . . . . . . .  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 50 Ohms

UHF Antenna (Helical)

Mounting . . . . . . . . . . . . . . . . . . . . . . . . .. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . BNC

Impedance . . . . . . . . . . . . . . . . . . .  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 50 Ohms

    - Peripheral Equipment and Accessories

The following peripheral equipment and accessories shall be offered in support of the Addressable Amplified RF Speaker:

Battery Back-Up Kit shall be offered to provide power back-up in the case of the loss of direct power.   The back-up time duration shall be a minimum of 120 minutes for the UHF and 600 Ohm input models and 75 minutes for the VHF model, at continuous full output power. The kit shall provide the battery and any necessary mounting hardware for installation inside the A.A.S.

Long-Life Battery Enclosure  shall be offered to house an 18Ah battery (ordered separately).  The enclosure shall also be designed to house the solar charge regulator module found in the solar panel interface kit.  The kit shall include a connection cable that plugs into a weather proof connector located on the enclosure’s side, with the other end terminating inside the A.A.S. enclosure.  Fully-charged, the 18Ah battery shall provide a minimum of 15 hours of AAS operation (UHF model) and a minimum of 12 hours of AAS operation (VHF model), at full output (8W).   Calculating the battery life based on 20 second duty-cycles, a fully charged battery shall provide over 3,000 cycles at maximum output.

Solar Panel Array shall be offered to provide trickle-charging of AAS battery operation (long-life battery).  The solar panel array shall provide a minimum 30-Watt output and shall include an integral connection cable that is minimally 15 feet in length.  The solar panel shall interconnect with the long-life battery enclosure.

Solar Panel Interface Kit shall be offered to provide materials necessary to mount the solar panel array to a pole (max. 4-inches in diameter) or flat surface.  The kit shall include all necessary hardware with the exception of mounting bands or U-bolts, which shall be provided by the installer. The kit shall also include a solar panel charge regulator module that shall mount inside the Long-Life Battery Enclosure.

Weatherproof Power Supply Kit shall be offered to provide external power to the RF Call Box.  The power supply shall provide a regulated 15.0V dc and maximum 1.7 amperes to the RF Call Box and shall be suitable for mounting via a ¾” NPT pipe nipple and hub to the bottom of the surface mount RF Call Boxes.  The kit shall include all necessary mounting hardware, wire harnesses, power supply, and weatherproof enclosure.  The power supply shall be capable of accepting an input of 120 – 240V ac.

Programming Software shall be offered to provide programming of the RF Receiver Module’s operating frequency and PL code and the AAS features, including but not limited to volume level, mode selection, and selective addresses.

Free-standing Tripod shall be offered to provide easy set-up and tear-down for temporary public address applications.

Tripod Mounting Kit shall be offered for installation of an AAS to the specified tripod.

Pole Mounting Kit shall be offered to mount the AAS to a pole with a maximum 4-inch diameter.

Pole Mounting Kit shall be offered to mount the Long-Life Battery Enclosure to a pole with a maximum 4-inch diameter.

Battery Charger shall be offered for recharging both the 2.8Ah and the 18Ah batteries.

    - Equipment Manufacturer and Model Numbers

The Addressable Amplified RF Speaker shall be GAI-Tronics Models 13363 (VHF, 154-174 MHz) and 13373 (UHF, 450-470 MHz).  AAS peripherals and accessories shall be GAI-Tronics models numbers, specified as:

- BB133 Battery Back-up Kit

- XB001 Long-Life Battery Enclosure

- GTRFP7784-108 30-Watt Solar Panel Array

- SPK200  Solar Panel Interface Kit

- 190-002PS External Power Supply Kit

- 19101-024 RF Module Programming Kit

- XAC1000A  CARD Suite Programming Software

- XAC0004A Programming Cable

- GT6432-006 Free-standing Tripod

- TPD001 Tripod Mounting Kit

- 231-001  Pole Mounting Kit for AAS

- 230-001  Pole Mounting Kit for XB001

- 40408-009 Battery Charger for 2.8Ah battery

- 40408-011 Battery Charger for 18Ah battery

- 12506-001 Remote Volume Control L-Pad

  - Audio Control Center Deskset

    - Description

The Audio Control Center deskset (ACC) shall be a head-end component of the Mass Notification/Public Address system.  The ACC shall offer a user-friendly solution for controlling alarms and voice messages to be broadcast throughout the system.  The ACC shall be in a desktop configuration but shall also be suitable for wall-mounting.  The deskset shall include an integral handset with pressbar, microphone, and speaker.  The ACC shall be PC-programmable and capable of initiating pre-recorded alarm tones and voice messages via an Audio Messenger Interface.  The ACC shall also be capable of selective determining broadcast location (individual, zones, all call) via a DTMF keypad or programmable single button activations.  The ACC shall include a 32-character LCD display to view system status and shall be capable of monitoring all broadcasted audio.  A plug-in power supply shall be included.  The system shall be designed to include a second, hot-standby ACC deskset for use if the main deskset suffers a catastrophic failure.  This unit shall be intended only for back-up operation, not for dual deskset operation.  The hot-standby unit shall connect to the same Audio Messenger Interface as does the main unit.  Both desksets shall not be installed further than 50 feet from the Audio Messenger Interface due to RS232 limitations.

    - Interconnection

All signal/audio connections to and from the ACC deskset shall be in the form of modular connectors.  Power connection shall match the power supply provided with the deskset.

    - Features

The Audio Control Center deskset shall include the following standard features and functionality:

- Initiates up to 125 Tone/Voice Messages via Audio Messenger Interface

- Generate Live Voice Broadcast via Handset, Integral Microphone, or Optional Desk Microphone

- Live Voice Broadcast Override of Active Alarm Tone/Messages

- Zone/Alarm Select Buttons

- Stop/Clear Buttons

- Programmable Alarm Activation Buttons (8)

- DTMF Keypad for Addressable Broadcast Capability

- System Monitoring via Integral Speaker with Volume Control

- 32-Character LCD Display, Indicating Zone, Alarm, Time, and Operator Instructions

- Time Display

- Zone/Alarm Alias Display

- Alarm Deactivation Control

- RS232 Connection to Audio Messenger Interface

- PC Programmable

- Plug-in Power Supply Included

    - Performance Specifications

Color . . . . . . . . . .. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .. . . . . . . . . . . . . . . . . Black

Dimensions . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 7.6” W x 8.9” L x 4.7”H

Weight . . . . . . . . . .. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .. . . . . . . . . . 3.2 lbs. min.

Temperature. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . -35° to +70° C

Humidity . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .  95% at 50° C non-condensing

Power Input . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 10.5 to 16 V dc, 400 mA maximum

Frequency Response. . . . . . .  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .±3 dB from 300-3000 Hz

Audio Output to Speaker. . . . . .  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 1 Watt minimum

Audio Distortion. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . Less than 3% THD

Audio/Data Connections. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . Modular

    - Peripheral Equipment and Accessories

The following peripheral equipment and accessories shall be offered in support of the Audio Control Center deskset:

Addressable Amplified Speaker per sections 10.1.0 and 10.2.0 of this specification.

Audio Messenger Interface per section 10.4.0 of this specification.

AMI to Deskset Interface per section 10.5.0 of this specification.

Programming Software and Cable shall be offered to perform programming of the ACC features and functionality.

    - Equipment Manufacturer and Model Numbers

The Audio Control Center Deskset shall be GAI-Tronics Model ACC2500.  Peripherals and accessories shall be GAI-Tronics models numbers, specified as:

13353 Addressable Amplified Speaker, 600 Ohm

13363 Addressable Amplified RF Speaker, VHF (154-174 MHz)

13373 Addressable Amplified RF Speaker, UHF (450-740 MHz)

234SBA Series Stanchion Broadcast Assembly (600 Ohm, UHF, or VHF)

234SBM Series Stanchion Broadcast Module (600 Ohm, UHF, or VHF)

10959-203 Audio Messenger Interface

12612-002 AMI to Deskset Interface

XAC1000A CARD Suite Programming Software

XAC0004A Programming Cable

  - Audio Messenger Interface

    - Description

The Audio Messenger Interface (AMI) shall be considered a head-end component of the Mass Notification/Public Address system.  The AMI shall be a self-contained unit that interconnects and communicates directly with the Audio Control Center deskset via RS232, providing up to 125 different pre-recorded tone, speech, or tone/speech audio outputs for emergency or mass notification applications.  The audio output signal shall be at a 600 Ohm, 0 dBM level.  In addition to the audio output, the AMI shall provide a voltage-free, dry contact closure output when an output is active, if required.  All audio outputs shall be initiated by the Audio Control Center deskset.

There shall be no need for the burning of EPROM’s in order to program the unit. The Audio Messenger Interface shall be customer configurable by use of the Configuration Software application tool.  Customer shall be able to set all parameters of the unit as well as create and program both tones and speech messages.  Speech messages shall be created in an MP3 format.  Both tones and speech messages shall be programmable for duration or repeat interval.  The unit’s configuration shall be stored on a CompactFlash® card.

The AMI shall provide a dry contact closure output when the unit’s audio output is active, if required.

A Telephone Interface shall be available to allow users to access the system via a telephone network. The Audio Messenger Interface shall auto-answer and provide a live audio path to the system.  The AMI shall be capable of accepting a either an analog extension line or C.O. line input.

    - Interconnection

All connections to and from the Audio Messenger Interface shall be via a maximum of 18 AWG wire and shall terminate via screw-type terminal strip inside the unit.

    - Features

The Audio Messenger Interface shall include the following standard features:

- Up to 125 Pre-recorded Alarm Tones, Speech Messages, or Tone/Speech Messages

- MP3 Recording Format stored on a CompactFlash®  card

- RS232 Data Communication with Audio Control Center deskset

- 600 Ohm, 0 dBM Output

- Isolated Dry Contact Closure Output When Audio is Active

- UL Listing

- Telephone Line Access

- Configuration Tool

    - Performance Specifications

Power Supply Requirements

Voltage.....................................................................................................12 to 24 V dc (UL listed) Class 2 power source

(plug-in 12 V dc power supply included with AMI)

Current .....................................................................................................................................................1 amp minimum

Power consumed ................................................................................................................................. 10 watts maximum

Audio

Speech capacity....................................................................................... 500 minutes with 512 Mb CompactFlash® card

Frequency response................................................................................................. 250–6500 Hz, +0/-3 dB ref. to 1 kHz

Distortion ........................................................................................................... <1% THD @ 1 kHz @ nominal settings

Outputs

600 Ohm output........................................................................................................................................ 1 Vrms nominal

Isolated output .....................................................................................................................................Dry contact closure

Inputs

Phone line input (extension or C.O.) ...................................................................................... 600 Ohm, 0 dBM nominal

Communications

ADVANCE............................................................................................................................................................ RS-232

Phone line ..................................................................................................................................................Analog, DTMF

Mechanical

Enclosure material .....................................................................................High-impact, glass-reinforced polyester, gray

Mounting..........................................................................................................Wall mounting; four 0.28 mounting holes

Connections......................................................................Screw-type Terminal, Four drill spots for location of conduit

Dimensions ..........................................................................13.00 H × 9.25 W × 4.00 D inches; (330 × 235 × 102 mm)

Weight........................................................................................................................................................ 5 lbs. (2.27 kg)

Environmental

Temperature range ....................................................................................................+32º F to +122º F (0º C to +50º C)

Humidity ..................................................................................................................................20-80%, non-condensing

FCC Information

Complies with CFR47, Part 15 ........................................................................................................................... Class A

Approvals

Safety of Information Technology Equipment.........................UL 60950, CAN/CSA-C22.2 No. 60950-00, IEC 60950

    - Peripheral Equipment and Accessories

The following peripheral equipment and accessories shall be offered in support of the Audio Messenger Interface:

Audio Control Center Deskset shall be provided to control alarm activation and live voice broadcasts via the AMI, per section 10.4.0 of this specification.

AMI to Deskset Interface per section 10.5.0 of this specification.

    - Equipment Manufacturer and Model Numbers

The Audio Messenger Interface shall be GAI-Tronics Model 10959-203.  Peripherals and accessories shall be GAI-Tronics models numbers, specified as:

ACC2500 Audio Control Center Deskset

12612-002 AMI to Deskset Interface

  - AMI to Deskset Interface

    - Description

The AMI to Deskset Interface shall be a passive device that provides ease of connectivity between the Audio Messenger Interface (AMI) and Audio Control Center deskset (ACC).  The AMI to Deskset Interface shall include two modular cable assemblies for connection to the ACC deskset.  The AMI to Deskset Interface shall be capable of accepting the modular connections from the cable assemblies as inputs.  It shall also be designed to accept an 8-pin modular connection for cat 5e cabling from the AMI.  This cabling shall be provided by the installer.

    - Interconnection

All connections to the AMI to Deskset Interface shall be via modular connectors.

    - Peripheral Equipment, Accessories, and Sub-components

The following peripheral equipment and accessories shall be offered in support of the AMI to Deskset Interface:

Audio Control Center Deskset shall be provided to control alarm activation and live voice broadcasts via the AMI, per section 10.3.0 of this specification.

Audio Messenger Interface per section 10.4.0 of this specification.

    - Equipment Manufacturer and Model Numbers

The AMI to Deskset Interface shall be GAI-Tronics Model 12612-002.  Peripherals and accessories shall be GAI-Tronics models numbers, specified as:

ACC2500 Audio Control Center Deskset

10959-203 Audio Messenger Interface

PART 2

11.0.0   Quantity Specification

The products described in Part 1 of this specification establish a standard of quality.  The following format establishes quantity:

11.1.0	Addressable Amplified Speakers

______________ Addressable Amplified Speaker, 600-Ohm, 0dBm Input in accordance with section 10.1.0  GAI-Tronics Model 13353

______________ Addressable Amplified RF Speaker VHF Operation in accordance with section 10.2.0    GAI-Tronics Model 13363

______________ Addressable Amplified RF Speaker UHF Operation in accordance with section 10.2.0    GAI-Tronics Model 13373

  - Audio Control Center Deskset

______________ 	Audio Control Center Deskset in accordance with section 10.3.0

GAI-Tronics Model ACC2500

11.3.0	Audio Messenger Interface (AMI)

______________ 	Audio Messenger Interface in accordance with section 10.4.0

GAI-Tronics Model 10959-203

11.4.0	AMI to Deskset Interface

______________ AMI to Deskset Interface in accordance with section 10.5.0

GAI-Tronics Model 12612-002

11.5.0    	Peripheral Equipment and Accessories

______________ 	AAS Batter Back-up Kit in accordance with sections 10.1.6 and 10.2.6

GAI-Tronics Model BB133

______________ 	Long-Life Battery Enclosure in accordance with sections 10.1.6 and 10.2.6

GAI-Tronics Model XB001

______________ 	Long-Life Battery, 18Ah in accordance with sections 10.1.6 and 10.2.6

GAI-Tronics Model 40201-008

______________ 	Solar Panel Array in accordance with sections 10.1.6 and 10.2.6

GAI-Tronics Model RFP7784-108

______________ 	Solar Panel Interface Kit in accordance with sections 10.1.6 and 10.2.6

GAI-Tronics Model SPK200

______________ Weatherproof Power Supply Kit in accordance with sections 10.1.6 and 10.2.6

GAI-Tronics Model 190-002PS

______________ 	CARD Suite Programming Software in accordance with sections 10.1.6, 10.2.6, and 10.3.6

GAI-Tronics Model XAC1000A

______________ 	Programming Cable in accordance with sections 10.1.6, 10.2.6, and 10.3.6

GAI-Tronics Model XAC0004A

______________ 	RF Module Programming Kit in accordance with section 10.2.6

GAI-Tronics Model 19101-024

______________	Free-Standing Tripod in accordance with section 10.1.6 and 10.2.6

GAI-Tronics Model GTRFP6432-006

______________ 	Tripod Mounting Kit in accordance with section 10.1.6 and 10.2.6

GAI-Tronics Model TPD001

______________ 	Pole Mounting Kit for XB001 in accordance with section 10.1.6 and 10.2.6

GAI-Tronics Model 230-001

______________ 	Pole Mounting Kit for AAS in accordance with section 10.1.6 and 10.2.6

GAI-Tronics Model 231-001

______________ 	Battery Charger in accordance with section 10.1.6 and 10.2.6

GAI-Tronics Model 40408-009

______________ 	Battery Charger for 40201-008 18Ah Battery in accordance with section 10.1.6 and 10.2.6 GAI-Tronics Model 40408-011

______________ 	Remote Volume Control in accordance with section 10.1.6 and 10.2.6

GAI-Tronics Model 12506-001